Preliminary Design Analysis of Membrane Bioreactors

Application in Treatment Sequences for Modernization of Wastewater Treatment Plants

Process design model, engineering diagrams, scale-up technique, membrane fouling simulation and response-surface (DOE/JMP) optimisation

Including complete Python and JMP (JSL) source code

Reference case: 12,000 m³/d municipal plant · MLE-MBR retrofit

October 2026

Contents

Note: if the contents list appears empty, right-click it in Word and choose Update Field.

# 1. Introduction and scope

Many conventional activated sludge (CAS) plants must now meet tighter nitrogen and phosphorus limits, treat higher flows and produce effluent suitable for reuse, often without room to build new tanks. Inserting a membrane bioreactor (MBR) into the existing treatment sequence addresses all three: membranes replace the secondary clarifiers, which removes the settling limit on mixed-liquor concentration, so the same tank volume holds roughly two to three times more biomass and the effluent is free of suspended solids.

This report documents a complete preliminary-design model for such a modernization. It sizes the biological process (modified Ludzack-Ettinger configuration with simultaneous chemical phosphorus precipitation), the submerged hollow-fibre membrane system, process and membrane-scour aeration, and the plant's energy demand. It then simulates membrane fouling and cleaning over 240 days, checks whether the MBR fits the existing tanks, sets out a pilot-to-full-scale scale-up procedure, and uses a designed experiment with response-surface methodology to find the best compromise between energy, footprint, membrane area and fouling.

All calculations are performed by two Python programs (mbr_design.py and doe_runner.py) and one JMP script (MBR_RSM_analysis.jsl), reproduced in full in Appendices A to C. Every number and figure in this report is generated by that code, so the design can be repeated for another plant by changing the input data and re-running it.

## 1.1 Status of the numbers

The plant data used here are an illustrative reference case typical of a medium-strength municipal wastewater, not measurements from a specific site. Kinetic and design parameters are standard literature defaults (Metcalf & Eddy, 2014; Judd, 2011). Before detailed design, the influent characterisation, membrane vendor data and pilot-plant fouling results should replace these defaults.

# 2. Design basis

Table 1. Influent characteristics (after coarse screening, no primary settling)

| Parameter | Value | Unit |
| --- | --- | --- |
| Average dry-weather flow | 12,000 | m³/d |
| Max-month / max-day / peak-hour factors | 1.30 / 1.60 / 2.00 | – |
| BOD₅ | 280 | mg/L |
| COD | 600 | mg/L |
| bCOD / BOD₅ | 1.6 | – |
| TSS / VSS | 300 / 240 | mg/L |
| Non-biodegradable VSS fraction | 0.35 | – |
| TKN / NH₄-N | 60 / 40 | mg N/L |
| Total phosphorus | 9 | mg P/L |
| Alkalinity | 300 | mg CaCO₃/L |
| Winter / summer design temperature | 12 / 24 | °C |

Table 2. Effluent targets and key design choices

| Item | Value |
| --- | --- |
| NH₄-N / TN / TP | ≤ 1 / ≤ 10 / ≤ 0.5 mg/L |
| TSS, turbidity | < 1 mg/L, < 0.2 NTU (membrane barrier) |
| Nitrification safety factor on SRT | 1.5 (with 15 d aerobic SRT floor) |
| Bioreactor MLSS / RAS ratio | 9.0 g/L / 4Q (membrane tank → aerobic) |
| Aerobic DO / DO in nitrate recycle | 2.0 / 1.0 mg/L |
| Side-water depth / diffuser submergence | 5.5 m / 5.2 m |
| Fine screening ahead of membranes | ≤ 1 mm punched plate (hollow-fibre protection) |
| Phosphorus removal | FeCl₃ simultaneous precipitation, Fe:P = 1.8 mol/mol |

Table 3. Activated sludge kinetic parameters at 20 °C (Metcalf & Eddy, 2014)

| Parameter | Heterotrophs | Nitrifiers (AOB) |
| --- | --- | --- |
| μmax (1/d) · θ | 6.0 · 1.07 | 0.90 · 1.072 |
| Half-saturation K (mg/L) | Ks = 8 (bCOD) | Kn = 0.50 (NH₄-N); Ko = 0.50 (O₂) |
| Yield Y (g VSS/g) | 0.45 | 0.15 |
| Decay b (1/d) · θ | 0.12 · 1.04 | 0.17 · 1.029 |
| Cell debris fraction fd | 0.15 | – |
| SDNR (g NO₃-N/g VSS·d) · θ | 0.08 · 1.026 | – |

Table 4. Membrane system design inputs (generic reinforced PVDF hollow fibre, 0.04–0.1 µm)

| Parameter | Value |
| --- | --- |
| Module area / modules per cassette | 34.4 m² / 48 (1,651 m² per cassette) |
| Trains | 4 |
| Gross flux at 20 °C: average / max-month / peak-hour | 25 / 30 / 40 L/m²·h |
| Filtration / relaxation cycle | 9 min / 1 min |
| Maintenance-clean downtime | 0.6 % of operating time |
| Clean-membrane permeability (20 °C) | 400 L/m²·h·bar |
| Specific scour air demand SAD_m | 0.25 Nm³/m²·h |
| Recovery-clean (CIP) trigger | TMP > 0.30 bar |

# 3. Treatment sequence and process flow diagram

The modernized sequence is: coarse screen (6 mm) → aerated grit and grease removal → fine screen (≤ 1 mm) → anoxic zone → aerobic zone → submerged membrane tanks → permeate pumps → UV disinfection or reuse. Fine screening is essential because hair and fibres wrap around hollow fibres and are the most common cause of irreversible membrane damage.

Mixed liquor is returned from the membrane tanks to the aerobic zone at 4Q. This keeps the solids concentration at the membranes about 25 % higher than in the bioreactor, and sends the high-oxygen membrane-tank liquor to the aerobic zone rather than the anoxic zone, where it would suppress denitrification. A separate internal recycle carries nitrate from the aerobic to the anoxic zone. Waste sludge is drawn from the membrane tanks, where it is most concentrated.

Figure 1. Process flow diagram with computed design values (generated by mbr_design.py)

# 4. Biological process design

## 4.1 Method

The minimum sludge age for nitrification is computed at the winter temperature from the net growth rate of the nitrifiers, and a safety factor is applied:

μA,T = μmax,A·θ^(T−20)·[N/(Kn+N)]·[DO/(Ko+DO)] ;   SRTmin = 1/(μA,T − bA,T)     (1)

The design aerobic SRT is the larger of 1.5 × SRTmin and 15 d. The effluent biodegradable COD and the biomass production follow the steady-state activated sludge model:

S = Ks(1 + bH·SRT) / [SRT(μmax,H − bH) − 1]     (2)

PX,bio = Q·YH(S0−S)/(1+bH·SRT) + fd·bH·PX,H·SRT + Q·YA·NOx/(1+bA·SRT)     (3)

Total solids production adds non-biodegradable VSS, inert inorganic solids and the ferric phosphate and hydroxide sludge. The total biomass inventory is PX,TSS × SRT; the part held in the membrane tanks is subtracted and the remainder sets the bioreactor volume at the design MLSS. The internal recycle ratio and the anoxic volume follow from the nitrate balance:

IR = NOx/NO3,e − 1 ;   Vanox = (NO3,removed + DO recycled/2.86) / (SDNRT · XVSS)     (4)

Because the anoxic fraction changes the total SRT, which changes sludge production and the nitrate load, equations 2 to 4 are solved iteratively until the anoxic fraction converges.

## 4.2 Results

Table 5. Biological process design results

| Quantity | Value |
| --- | --- |
| Minimum nitrification SRT at 12 °C | 7.1 d |
| Design aerobic SRT / total SRT | 15.0 d / 18.4 d |
| Anoxic / aerobic / total bioreactor volume | 1,534 / 6,149 / 7,683 m³ |
| Anoxic volume fraction | 18 % |
| MLSS bioreactor / membrane tank | 9.0 / 11.25 g/L |
| Hydraulic retention time (incl. membrane tanks) | 16.4 h |
| Food-to-microorganism ratio | 0.084 kg BOD/kg VSS·d |
| Sludge production (incl. chemical sludge) | 4,095 kg TSS/d (986 kg/d chemical) |
| Observed yield | 1.22 kg TSS/kg BOD |
| Nitrate formed / removed | 46.3 mg N/L / 459 kg N/d |
| Internal (nitrate) recycle ratio | 4.78 Q |
| FeCl₃ demand | 274 kg Fe/d |
| Residual alkalinity / supplement | 61 mg CaCO₃/L / 233 kg CaCO₃/d |

Residual alkalinity falls below the usual 70–80 mg/L minimum for stable nitrification, mainly because ferric chloride consumes alkalinity, so a small lime, soda ash or magnesium hydroxide dose is included in the design.

# 5. Membrane system design

## 5.1 Method

Flux is corrected for water viscosity at the winter temperature and reduced by the time lost to relaxation and maintenance cleaning:

JT = J20 · μ20/μT ;   Jnet = JT · tf/(tf + tr) · (1 − fMC)     (5)

The required area is the largest of three cases: average flow with one train out of service for recovery cleaning, max-month flow at the sustained flux, and peak-hour flow at the short-term peak flux:

A = max{ Qavg / [Jnet,avg·(N−1)/N] ,  Qmm / Jnet,mm ,  Qph / Jnet,peak }     (6)

The area is rounded up to whole cassettes per train. Scour air is the installed area multiplied by SAD_m, and the scour air per unit of permeate is SAD_p = SAD_m × 1000 / Jnet.

## 5.2 Results

Table 6. Membrane system design results

| Quantity | Value |
| --- | --- |
| Viscosity correction at 12 °C / availability | × 0.814 / 89.5 % |
| Area: average N−1 / max-month / peak-hour | 36,603 / 29,740 / 34,315 m² |
| Governing case | average flow, N-1 trains |
| Installed | 4 trains × 6 cassettes = 24 cassettes (1,152 modules) |
| Installed membrane area | 39,629 m² |
| Operating gross flux at average flow | 14.1 L/m²·h |
| Scour air / SAD_p | 9,907 Nm³/h / 19.8 Nm³/m³ |
| Membrane tank volume (all trains) and train size | 541 m³; each train 14.2 × 2.8 × 3.4 m |
| Packing density | 73 m²/m³ |

The operating flux of about 14 L/m²·h and SAD_p of about 20 Nm³/m³ are within the ranges reported for full-scale hollow-fibre MBRs (Judd, 2011).

# 6. Oxygen demand and aeration

The actual oxygen requirement combines carbon oxidation, nitrification and the credit returned by denitrification:

AOR = Q(S0 − S) − 1.42·PX,bio + 4.57·Q·NOx − 2.86·NO3,removed     (7)

It is converted to standard (clean-water) conditions with the alpha factor, which falls steeply with MLSS (Krampe & Krauth, 2003), and with mid-depth oxygen saturation corrected for site elevation:

SOTR = AOR / [ α·F·(β·C*T,H − C)/C*20 · 1.024^(T−20) ] ,   α = exp(−0.08788·MLSS)     (8)

Coarse-bubble scour air in the membrane tanks also transfers oxygen; this is credited before the fine-bubble process air is sized. Summer max-day governs blower capacity.

Table 7. Aeration results

| Case | α | AOR (kg/d) | Scour O₂ credit (kg/d) | SOTR (kg/d) | Process air (Nm³/h) |
| --- | --- | --- | --- | --- | --- |
| winter | 0.45 | 4,929 | 619 | 11,351 | 5,512 |
| summer | 0.45 | 4,929 | 534 | 11,907 | 5,783 |
| summer max-day | 0.45 | 6,162 | 534 | 15,246 | 7,404 |

The alpha factor of 0.45 at 9 g/L means each kilogram of oxygen needs roughly twice the air it would at CAS concentrations. This is the main energy penalty of operating at high MLSS and is examined further in Sections 11 and 12.

# 7. Energy demand

Blower power uses the adiabatic compression equation (Metcalf & Eddy, 2014) with discharge pressure equal to diffuser submergence plus pipe and diffuser losses; pump power is ρgQH/η.

Pblower = w·R·T1 / (29.7·n·e) · [ (p2/p1)^0.283 − 1 ]     (9)

Table 8. Average-day energy demand, full scale

| Consumer | Power (kW) | Specific energy (kWh/m³) |
| --- | --- | --- |
| Process aeration | 129 | 0.258 |
| Membrane scour air | 138 | 0.276 |
| Permeate pumping | 12 | 0.023 |
| RAS pumping | 13 | 0.026 |
| Nitrate recycle pumping | 9 | 0.017 |
| Anoxic mixing | 8 | 0.015 |
| Screens, CIP, miscellaneous | 20 | 0.040 |
| TOTAL | 328 | 0.656 |

The total of 0.66 kWh/m³ is typical of a modern MBR. Membrane scour and process aeration together account for about 81 %, so they are the main targets for optimisation.

# 8. Membrane fouling and cleaning simulation

Membrane performance over 240 days is simulated hour by hour with the resistance-in-series model:

TMP = μ(T) · J · (Rm + Rres + Rirr + Rperm)     (10)

dRres = k · (J/Jref)² · dV ,   k ∝ (0.25/SADm)^0.8 · (XMT/11.25)^0.5     (11)

Rm is the clean-membrane resistance. Residual fouling Rres builds with filtered volume and is 75 % removed by weekly maintenance cleans. A fraction becomes irreversible fouling Rirr, which only a recovery clean (CIP) removes; a smaller fraction becomes permanent fouling Rperm. The fouling rate rises with the square of flux (critical-flux behaviour), falls with more scour air and rises with mixed-liquor solids. Flow follows a diurnal pattern with six random storm events, temperature follows the seasons, and one train goes offline during each recovery clean.

Figure 2. Simulated flux, temperature, TMP and temperature-corrected permeability over 240 days

In the reference design, TMP reaches the 0.30 bar trigger once, at day 77 in the cold period when water viscosity is highest, giving roughly 1.5 recovery cleans per year. Permeability drops from about 400 to about 100 L/m²·h·bar between cleans. Both are in line with full-scale experience. The fouling coefficients are calibration constants and should be fitted to pilot data.

# 9. Modernization (retrofit) check

The existing plant is assumed to have two aeration tanks of 4,000 m³ operating at 3.5 g/L MLSS, a concentration limited by the solids loading on its two 28 m secondary clarifiers. At the same SRT and nutrient targets, the treatment capacity of a fixed tank volume is proportional to the biomass it can hold:

Qmax = (Vexisting·XMLSS + VMT·XMT) / (PX,TSS per m³ · SRT)     (12)

Table 9. Retrofit capacity comparison

| Quantity | Existing CAS | MBR in same tanks |
| --- | --- | --- |
| MLSS | 3.5 g/L | 9.0 g/L (11.25 in membrane tanks) |
| Capacity at SRT 18.4 d with N and P removal | 4,466 m³/d | 12,455 m³/d |
| Capacity gain | – | × 2.79 |
| Bioreactor volume required for 12,000 m³/d | – | 7,683 of 8,000 m³ available |
| Secondary clarifiers | Required | Released: 4,926 m³, 1,232 m² |

Figure 3. Capacity of the existing tanks as CAS and as MBR, and volume balance

The MBR fits within the existing aeration tanks while raising capacity from about 4,500 to 12,000 m³/d with full nitrogen removal. The released clarifiers can house the membrane tanks (about 160 m² footprint), flow equalisation or sludge storage.

# 10. Scale-up technique: pilot to full scale

Submerged membranes are scaled by numbering up identical modules rather than by enlarging them. A single pilot module is multiplied into a cassette (×48), a train (×6) and the plant (×4 trains), a total factor of 1,152. Because each module sees the same flux, scour air and mixed liquor, the filtration behaviour measured on the pilot transfers directly, provided the quantities that do change with size are corrected.

Figure 4. Modular scale-up hierarchy, energy at pilot and full scale, and scale-variant parameters

Table 10. Parameters held constant across scales (scale-invariant)

| Parameter | Value | Why it must be held |
| --- | --- | --- |
| Gross flux | 14.1 L/m²·h | Fouling rate depends on flux relative to critical flux |
| SAD_m / SAD_p | 0.25 Nm³/m²·h / 19.8 Nm³/m³ | Shear at the fibre surface controls cake build-up |
| SRT, MLSS, HRT, F/M | 18.4 d, 9.0 g/L, 16.4 h, 0.084 | Sludge properties (EPS, filterability, α) depend on them |
| Recycle ratios R / IR | 4.0 / 4.8 | Solids profile and nitrate removal |
| Filtration/relax cycle, cleaning protocol | 9/1 min; NaOCl, citric acid doses per m² | Fouling reversibility |

Table 11. Parameters that change with scale and must be corrected (scale-variant)

| Parameter | Pilot | Full scale | Consequence |
| --- | --- | --- | --- |
| Diffuser submergence | 2.2 m | 5.2 m | Oxygen transfer efficiency rises with depth |
| Process SOTE | 12.1 % | 28.6 % | Pilot needs ~2.8× more air per m³ |
| Process air | 33.1 Nm³/m³ | 11.8 Nm³/m³ | Pilot energy overstates full scale |
| Blower efficiency | 0.45 | 0.75 | Small machines are inefficient |
| Mixing power | 15 W/m³ | 5 W/m³ | Small tanks need more mixing power |
| Peak-cassette flux factor | 1.00 | 1.07 | Uneven suction along long permeate headers |
| Specific energy | 1.34 kWh/m³ | 0.66 kWh/m³ | Pilot energy must not be used directly |

## 10.1 Recommended scale-up procedure

- Run the pilot with the full-scale fine screen and the same membrane module, at the design flux, SAD_m, SRT and MLSS, for at least one full winter.

- Fit the fouling constants k, firr and the exponents in equation 11 to the measured TMP and permeability, including weekly maintenance cleans.

- Measure the alpha factor and oxygen uptake rate at pilot MLSS; use the measured alpha, not the pilot's air consumption, for full-scale blower sizing.

- Recalculate oxygen transfer, blower, pump and mixer power for full-scale depths and equipment (Table 11).

- Check permeate manifold head loss so that the most loaded cassette stays within about 5–7 % of the average flux, and add flux margin for that maldistribution.

- Check the design against peak-hour flow with all trains and average flow with one train in recovery cleaning (equation 6).

# 11. Design sensitivity

Figure 5. (a) Installed membrane area vs winter temperature and design flux; (b) bioreactor volume and process air vs MLSS

Panel (a) shows that a 4 °C colder design temperature adds roughly one cassette per train at any flux, because flux falls with water viscosity; the steps occur where an extra whole cassette is needed. Panel (b) shows the central MBR trade-off: raising MLSS shrinks the bioreactor but the falling alpha factor drives process air up. Between 8 and 12 g/L, the usual MBR operating window, the two effects roughly balance.

# 12. Design of experiments and response-surface optimisation

## 12.1 Experimental design

To optimise several design choices at once, the full model was run over a face-centred central composite design (CCD) in five factors: 32 factorial runs, 10 axial runs and 6 centre points, 48 runs in randomised order. This is the same design JMP builds under DOE › Classical › Response Surface Design. Winter temperature is included as a climate (noise) factor so that its effect is quantified, but it is locked at the 12 °C design value when optimising.

Table 12. DOE factors and levels

| Factor | Low (−1) | Centre (0) | High (+1) |
| --- | --- | --- | --- |
| MLSS (g/L) | 7 | 9 | 11 |
| Design flux at 20 °C (L/m²·h) | 20 | 25 | 30 |
| SAD_m (Nm³/m²·h) | 0.15 | 0.25 | 0.35 |
| Winter temperature (°C) | 10 | 13 | 16 |
| Aerobic SRT floor (d) | 12 | 16 | 20 |

## 12.2 Response-surface models

A full quadratic model (intercept, 5 linear, 10 two-factor interaction and 5 squared terms) was fitted to each response by least squares, the same model JMP fits with the '& RS' effects in the script of Appendix C.

Table 13. Goodness of fit of the quadratic models

| Response | R² | R² adjusted | RMSE |
| --- | --- | --- | --- |
| Energy (kWh/m³) | 0.9980 | 0.9964 | 0.0066 |
| Footprint (m³) | 0.9996 | 0.9992 | 63 |
| Required membrane area (m²) | 1.0000 | 1.0000 | 33 |
| Mean TMP (bar) | 0.8957 | 0.8184 | 0.0067 |
| Process air (Nm³/h) | 0.9998 | 0.9996 | 25 |
| Sludge production (kg/d) | 0.9983 | 0.9971 | 4.9 |
| Recovery cleans per year | 0.9339 | 0.8849 | 0.84 |

The engineering responses are fitted almost exactly. Mean TMP and the number of recovery cleans fit less well because the cleaning events make them jump in steps; their models are adequate for ranking factors but not for precise prediction.

Figure 6. Ten largest scaled effects (coded coefficients) for each optimised response

Energy is driven mainly by scour air (SAD_m), then design flux (higher flux means less membrane and so less scour air), then MLSS through the alpha factor. Footprint depends on MLSS and SRT. Mean TMP rises with flux and falls with scour air, so flux and scour air pull energy and fouling in opposite directions.

## 12.3 Desirability optimisation

Energy, footprint, membrane area and mean TMP were each converted to a smaller-is-better Derringer desirability between their lowest and highest observed values, and the geometric mean D was maximised over the four controllable factors with temperature locked at 12 °C. The optimum (D = 0.61) was then re-run through the full model to check the prediction.

Table 14. Optimum factor settings

| Factor | Optimum | Baseline design |
| --- | --- | --- |
| MLSS (g/L) | 9.89 | 9.0 |
| Design flux at 20 °C (L/m²·h) | 29.9 | 25.0 |
| SAD_m (Nm³/m²·h) | 0.344 | 0.25 |
| Winter temperature (°C, locked) | 12 | 12 |
| Aerobic SRT floor (d) | 12.0 | 15.0 |

Table 15. Responses at the optimum: response-surface prediction, full-model check and baseline

| Response | RSM prediction | Full model | Baseline |
| --- | --- | --- | --- |
| Energy (kWh/m³) | 0.716 | 0.704 | 0.656 |
| Footprint (m³) | 6,537 | 6,312 | 8,224 |
| Required membrane area (m²) | 30,580 | 30,610 | 36,600 |
| Mean TMP (bar) | 0.114 | 0.115 | 0.119 |
| Process air, max-day (Nm³/h) | 7,745 | 7,689 | 7,404 |
| Sludge production (kg TSS/d) | 4,166 | 4,193 | 4,095 |
| Recovery cleans per year | 1.7 | 3.0 | 1.5 |

Figure 7. Fitted response surfaces versus MLSS and flux, with the overall desirability (★ = optimum)

Figure 8. Prediction profiler at the optimum (equivalent of the JMP Profiler)

The optimum reduces bioreactor volume by about 23 % and membrane area by about 16 % for about 7 % more energy, trading scour air for a higher, still conservative flux. The full-model check agrees with the RSM prediction within 4 % for every engineering response. Two cautions apply: the optimiser chose the lowest allowed aerobic SRT (12 d), which leaves a small nitrification safety margin in cold weather, so 15 d or more is recommended for the final design; and the recovery-clean frequency at the optimum (about 3 per year) is higher than the model predicts, so it should be confirmed on the pilot.

# 13. Running the analysis in JMP

The response-surface analysis in Section 12 was computed in Python. The same analysis can be reproduced and explored interactively in JMP with the script in Appendix C:

- Place mbr_doe_runs.csv (Appendix D) and MBR_RSM_analysis.jsl in the same folder.

- Open MBR_RSM_analysis.jsl in JMP 16 or later and choose Run Script (Ctrl+R).

- The script sets factor coding and desirability limits, fits a full quadratic Standard Least Squares model for each of the seven responses and saves the prediction formulas.

- It opens the Prediction Profiler with temperature locked at 12 °C and runs Maximize Desirability, then a Contour Profiler with surface plots and a Graph Builder overview.

- The optimum and the fit statistics shown in JMP should match Tables 13 to 15.

The Python model itself can also run inside JMP 18 and later through File › New › Python Script, so the whole workflow can be kept in one tool if preferred.

# 14. Limitations and next steps

- Influent data are an illustrative reference case; a site sampling campaign (COD fractionation, TKN, alkalinity, temperature record) is needed.

- Steady-state design equations are used; a dynamic simulation (ASM1/ASM2d) should confirm effluent nitrogen under diurnal and storm loads.

- Fouling constants are literature-based calibration values and must be fitted to pilot TMP data.

- Membrane module dimensions and flux limits are generic; vendor data will change the cassette count and tank layout.

- Costs (capital, membrane replacement, chemicals, energy tariffs) are not yet included; adding net present value as a DOE response is a natural extension.

## References

Judd, S. (2011). The MBR Book: Principles and Applications of Membrane Bioreactors for Water and Wastewater Treatment, 2nd ed. Butterworth-Heinemann, Oxford.

Krampe, J., Krauth, K. (2003). Oxygen transfer into activated sludge with high MLSS concentrations. Water Science and Technology 47(11), 297–303.

Metcalf & Eddy / AECOM (2014). Wastewater Engineering: Treatment and Resource Recovery, 5th ed. McGraw-Hill, New York.

Derringer, G., Suich, R. (1980). Simultaneous optimization of several response variables. Journal of Quality Technology 12(4), 214–219.

# Appendix A. mbr_design.py: design model and diagrams

Python 3 with numpy and matplotlib. Run with: python mbr_design.py. Outputs are written to the folder mbr_outputs.

1  #!/usr/bin/env python3

2  """

3  =====================================================================================

4   MEMBRANE BIOREACTOR (MBR) - PRELIMINARY DESIGN, DIAGRAMS & SCALE-UP MODEL

5   Application: modernization of an existing conventional activated sludge (CAS) plant

6                by inserting an MLE-type MBR treatment sequence:

7                coarse screen -> grit/grease -> fine screen (<=1 mm) -> anoxic -> aerobic

8                -> submerged hollow-fibre membrane tank -> permeate -> UV

9  =====================================================================================

10   Methods / references used (standard design literature):

11     * Metcalf & Eddy (2014) Wastewater Engineering, 5th ed. - activated sludge kinetics,

12       biomass production, oxygen demand, MLE nitrogen removal, blower power.

13     * Judd, S. (2011) The MBR Book, 2nd ed. - flux, SAD_m / SAD_p, cleaning regimes,

14       specific energy demand benchmarks.

15     * Krampe & Krauth (2003) - alpha factor vs MLSS: alpha = exp(-0.08788 * MLSS[g/L]).

16     * Resistance-in-series filtration law: TMP = mu(T) * J * (Rm + Rres + Rirr).

17   All numbers are preliminary-design values; site data (influent characterisation,

18   vendor membrane data, pilot results) must replace defaults before detailed design.

19

20   Run:  python mbr_design.py            -> writes figures + report into ./mbr_outputs

21   Requires: numpy, matplotlib

22  =====================================================================================

23  """

24  from __future__ import annotations

25

26  import json

27  import math

28  import os

29  from dataclasses import dataclass, asdict, field

30

31  import numpy as np

32  import matplotlib

33

34  matplotlib.use("Agg")

35  import matplotlib.pyplot as plt

36  from matplotlib.patches import FancyBboxPatch, Rectangle, Circle

37

38  OUT = "mbr_outputs"

39  os.makedirs(OUT, exist_ok=True)

40

41  RHO_W = 998.0          # kg/m3

42  G = 9.81               # m/s2

43  P_ATM = 101.325        # kPa

44  O2_PER_NM3_AIR = 0.300 # kg O2 per Nm3 air (1.293 kg/Nm3 * 0.232)

45

46

47  # ----------------------------------------------------------------------------------

48  # 1. INPUT DATA

49  # ----------------------------------------------------------------------------------

50  @dataclass

51  class Influent:

52      """Raw municipal wastewater after coarse screening (no primary settling)."""

53      Q_avg: float = 12_000.0     # m3/d  average dry-weather flow

54      pf_maxmonth: float = 1.30   # peaking factors

55      pf_maxday: float = 1.60

56      pf_peakhour: float = 2.00   # peak hour that membranes must pass (after EQ if any)

57      BOD: float = 280.0          # g/m3

58      COD: float = 600.0

59      bCOD_BOD: float = 1.60      # biodegradable COD / BOD5

60      TSS: float = 300.0

61      VSS: float = 240.0

62      nbVSS_frac: float = 0.35    # non-biodegradable fraction of VSS

63      TKN: float = 60.0           # g N/m3

64      NH4: float = 40.0

65      TP: float = 9.0             # g P/m3

66      Alk: float = 300.0          # g CaCO3/m3

67      T_min: float = 12.0         # degC, winter design (nitrification, flux)

68      T_max: float = 24.0         # degC, summer design (oxygen)

69

70

71  @dataclass

72  class DesignBasis:

73      NH4_eff: float = 1.0        # g/m3

74      TN_eff: float = 10.0

75      orgN_eff: float = 1.0

76      TP_eff: float = 0.5

77      DO_aer: float = 2.0         # g/m3 in aerobic zone

78      DO_mlr: float = 1.0         # DO carried with mixed-liquor recycle to anoxic

79      SF_nit: float = 1.5         # safety factor on nitrification SRT

80      SRT_aer_floor: float = 15.0 # d - MBR practice (sludge stability, fouling control)

81      X_bio: float = 9.0          # kg TSS/m3 in anoxic/aerobic tanks

82      R_ras: float = 4.0          # membrane tank -> aerobic recycle ratio (Q multiples)

83      swd_bio: float = 5.5        # m side water depth (existing CAS tanks)

84      sub_diffuser: float = 5.2   # m diffuser submergence

85      sote_per_m: float = 0.055   # fine-bubble clean-water SOTE per m submergence

86      fouling_F: float = 0.90     # diffuser fouling factor

87      beta: float = 0.95

88      elev_m: float = 120.0       # site elevation (Radnor-type site), m a.s.l.

89      Fe_P_molar: float = 1.8     # FeCl3 simultaneous precipitation

90      anox_mix_W_m3: float = 5.0  # submersible mixer power density

91

92

93  @dataclass

94  class Kinetics:

95      """Metcalf & Eddy (2014) Table 8-14 / 8-24 default values at 20 degC."""

96      mu_H: float = 6.0;   th_muH: float = 1.07

97      Ks: float = 8.0

98      Y_H: float = 0.45

99      b_H: float = 0.12;   th_bH: float = 1.04

100      fd: float = 0.15

101      mu_A: float = 0.90;  th_muA: float = 1.072

102      Kn: float = 0.50

103      Ko_A: float = 0.50

104      Y_A: float = 0.15

105      b_A: float = 0.17;   th_bA: float = 1.029

106      SDNR20: float = 0.08; th_SDNR: float = 1.026   # g NO3-N / g MLVSS.d

107      N_in_biomass: float = 0.12  # g N / g VSS

108      P_in_biomass: float = 0.015

109

110

111  @dataclass

112  class MembraneSpec:

113      """Generic reinforced PVDF hollow-fibre (0.04-0.1 um) submerged module data."""

114      module_area: float = 34.4        # m2 per module

115      modules_per_cassette: int = 48

116      cassette_L: float = 1.9          # m

117      cassette_W: float = 2.2

118      cassette_H: float = 2.6

119      J_avg20: float = 25.0            # L/m2.h gross design flux, 20 degC

120      J_mm20: float = 30.0             # L/m2.h sustained max-month flux, 20 degC

121      J_peak20: float = 40.0           # L/m2.h short-term peak flux, 20 degC

122      t_filt: float = 9.0              # min filtration

123      t_relax: float = 1.0             # min relaxation (air scour continues)

124      mc_downtime: float = 0.006       # fraction of time in maintenance cleaning

125      n_trains: int = 4

126      Lp_clean20: float = 400.0        # L/m2.h.bar clean-membrane permeability

127      SAD_m: float = 0.25              # Nm3 air / m2 membrane . h

128      mt_depth: float = 3.4            # m membrane tank water depth

129      scour_sub: float = 3.0           # m scour aerator submergence

130      scour_sote_per_m: float = 0.012  # coarse-bubble SOTE per m

131      TMP_max: float = 0.30            # bar - recovery-clean trigger

132

133

134  @dataclass

135  class ExistingCAS:

136      """Plant being modernised (illustrative)."""

137      n_aer_tanks: int = 2

138      V_aer_each: float = 4_000.0      # m3

139      X_cas: float = 3.5               # kg/m3 limited by secondary clarifier SLR

140      n_clarifiers: int = 2

141      clarifier_D: float = 28.0        # m

142      clarifier_swd: float = 4.0

143

144

145  # ----------------------------------------------------------------------------------

146  # 2. PROPERTY CORRELATIONS

147  # ----------------------------------------------------------------------------------

148  def water_viscosity(T: float) -> float:

149      """Dynamic viscosity of water, Pa.s (Vogel-type correlation)."""

150      return 2.414e-5 * 10 ** (247.8 / (T + 133.15))

151

152

153  def arr(k20: float, theta: float, T: float) -> float:

154      return k20 * theta ** (T - 20.0)

155

156

157  def do_saturation(T: float) -> float:

158      """Clean-water DO saturation at 1 atm, g/m3 (APHA polynomial)."""

159      return 14.652 - 0.41022 * T + 0.007991 * T**2 - 0.000077774 * T**3

160

161

162  def alpha_factor(mlss_gL: float) -> float:

163      """Krampe & Krauth (2003) - oxygen transfer alpha factor vs MLSS."""

164      return math.exp(-0.08788 * mlss_gL)

165

166

167  def pressure_at_elev(elev: float) -> float:

168      return P_ATM * (1 - 2.25577e-5 * elev) ** 5.25588  # kPa

169

170

171  # ----------------------------------------------------------------------------------

172  # 3. MEMBRANE SIZING

173  # ----------------------------------------------------------------------------------

174  def membrane_design(inf: Influent, m: MembraneSpec) -> dict:

175      mu_ratio = water_viscosity(20) / water_viscosity(inf.T_min)  # flux temperature corr.

176      avail = m.t_filt / (m.t_filt + m.t_relax) * (1 - m.mc_downtime)

177

178      J_avg_T = m.J_avg20 * mu_ratio

179      J_peak_T = m.J_peak20 * mu_ratio

180      Jnet_avg = J_avg_T * avail

181      Jnet_peak = J_peak_T * avail

182

183      Q_avg_h = inf.Q_avg / 24.0                       # m3/h

184      Q_mm_h = Q_avg_h * inf.pf_maxmonth

185      Q_ph_h = Q_avg_h * inf.pf_peakhour

186

187      Jnet_mm = m.J_mm20 * mu_ratio * avail

188      # Case A: average flow with one train offline for recovery cleaning (N-1)

189      A_avg = Q_avg_h * 1000 / Jnet_avg / ((m.n_trains - 1) / m.n_trains)

190      # Case B: max-month flow, all trains, sustained flux

191      A_mm = Q_mm_h * 1000 / Jnet_mm

192      # Case C: peak-hour flow, all trains online, short-term peak flux

193      A_ph = Q_ph_h * 1000 / Jnet_peak

194      cases = {"average flow, N-1 trains": A_avg, "max-month flow, sustained flux": A_mm,

195               "peak-hour flow, peak flux": A_ph}

196      governing = max(cases, key=cases.get)

197      A_req = cases[governing]

198

199      A_cas = m.module_area * m.modules_per_cassette

200      n_cas_train = math.ceil(A_req / A_cas / m.n_trains)

201      n_cas = n_cas_train * m.n_trains

202      A_inst = n_cas * A_cas

203

204      # Membrane tank geometry per train (0.3 m clearances)

205      L_train = n_cas_train * (m.cassette_L + 0.30) + 1.0

206      W_train = m.cassette_W + 2 * 0.30

207      V_train = L_train * W_train * m.mt_depth

208      V_mt = V_train * m.n_trains

209

210      air_scour = A_inst * m.SAD_m                       # Nm3/h

211      Jop_avg = Q_avg_h * 1000 / (A_inst * avail)        # actual gross flux at Q_avg

212      SAD_p = air_scour / Q_avg_h                        # Nm3 air / m3 permeate

213      packing = A_inst / V_mt                            # m2/m3

214

215      return dict(mu_ratio=mu_ratio, availability=avail, J_avg_T=J_avg_T, J_peak_T=J_peak_T,

216                  Jnet_avg=Jnet_avg, Jnet_peak=Jnet_peak, A_avg=A_avg, A_mm=A_mm, A_ph=A_ph, A_req=A_req,

217                  governing=governing, A_cassette=A_cas, n_cas_train=n_cas_train, n_cassettes=n_cas,

218                  n_modules=n_cas * m.modules_per_cassette, A_installed=A_inst,

219                  L_train=L_train, W_train=W_train, V_mt=V_mt, air_scour_Nm3h=air_scour,

220                  J_operating_avg=Jop_avg, SAD_p=SAD_p, packing_density=packing)

221

222

223  # ----------------------------------------------------------------------------------

224  # 4. BIOLOGICAL DESIGN (MLE configuration, iterative anoxic fraction)

225  # ----------------------------------------------------------------------------------

226  def nitrification_srt(k: Kinetics, d: DesignBasis, T: float) -> float:

227      mu = arr(k.mu_A, k.th_muA, T) * d.NH4_eff / (k.Kn + d.NH4_eff) * d.DO_aer / (k.Ko_A + d.DO_aer)

228      b = arr(k.b_A, k.th_bA, T)

229      return 1.0 / (mu - b)

230

231

232  def biological_design(inf: Influent, d: DesignBasis, k: Kinetics, mem: dict) -> dict:

233      T = inf.T_min

234      Q = inf.Q_avg

235      bCOD = inf.bCOD_BOD * inf.BOD

236      nbVSS = inf.nbVSS_frac * inf.VSS

237      iTSS = inf.TSS - inf.VSS

238

239      SRTmin = nitrification_srt(k, d, T)

240      SRT_aer = max(d.SF_nit * SRTmin, d.SRT_aer_floor)

241

242      muH, bH = arr(k.mu_H, k.th_muH, T), arr(k.b_H, k.th_bH, T)

243      muA, bA = arr(k.mu_A, k.th_muA, T), arr(k.b_A, k.th_bA, T)

244      X_mt = d.X_bio * (1 + d.R_ras) / d.R_ras           # membrane-tank MLSS (mass balance)

245

246      f_anox, NOx = 0.20, 0.8 * inf.TKN

247      for _ in range(50):

248          SRT = SRT_aer / (1 - f_anox)

249          S = k.Ks * (1 + bH * SRT) / (SRT * (muH - bH) - 1)            # effluent bCOD

250          Px_H = Q * k.Y_H * (bCOD - S) / (1 + bH * SRT) / 1000          # kg VSS/d

251          Px_D = k.fd * bH * Px_H * SRT

252          Px_A = Q * k.Y_A * NOx / (1 + bA * SRT) / 1000

253          Px_bio = Px_H + Px_D + Px_A

254          NOx = inf.TKN - d.NH4_eff - d.orgN_eff - k.N_in_biomass * Px_bio * 1000 / Q

255

256          # phosphorus: biological uptake + FeCl3 simultaneous precipitation

257          P_bio = k.P_in_biomass * Px_bio * 1000 / Q

258          P_chem = max(inf.TP - P_bio - d.TP_eff, 0)

259          Fe_kgd = Q * P_chem / 30.97 * d.Fe_P_molar * 55.85 / 1000

260          chem_sludge = Fe_kgd * 3.6                                      # FePO4 + Fe(OH)3

261

262          Px_VSS = Px_bio + Q * nbVSS / 1000

263          Px_TSS = Px_bio / 0.85 + Q * nbVSS / 1000 + Q * iTSS / 1000 + chem_sludge

264          M_total = Px_TSS * SRT                                          # kg TSS inventory

265

266          # MLE nitrate balance

267          NO3_eff = d.TN_eff - d.NH4_eff - d.orgN_eff

268          IR = max(NOx / NO3_eff - 1.0, 0.0)                              # total recycle to anoxic

269          NO3_rem = Q * (NOx - NO3_eff) / 1000                            # kg N/d

270          DO_eq = IR * Q * d.DO_mlr / 2.86 / 1000                         # kg NO3-N eq/d

271          vss_frac = Px_VSS / Px_TSS

272          SDNR = arr(k.SDNR20, k.th_SDNR, T)

273          V_anox = (NO3_rem + DO_eq) / (SDNR * d.X_bio * vss_frac)

274

275          M_mt = mem["V_mt"] * X_mt

276          V_aer = max((M_total - M_mt) / d.X_bio - V_anox, 0.0)

277          f_new = V_anox * d.X_bio / M_total

278          if abs(f_new - f_anox) < 1e-6:

279              break

280          f_anox = 0.5 * f_anox + 0.5 * f_new

281

282      V_bio = V_anox + V_aer

283      HRT = (V_bio + mem["V_mt"]) / Q * 24

284      FM = Q * inf.BOD / 1000 / (M_total * vss_frac)

285      Y_obs = Px_TSS / (Q * (inf.BOD) / 1000)

286

287      # Alkalinity check

288      N_nit = NOx

289      alk_eff = inf.Alk - 7.14 * N_nit + 3.57 * (NOx - NO3_eff) - 2.0 * Fe_kgd * 1000 / Q

290      alk_add = max(80 - alk_eff, 0) * Q / 1000                          # kg CaCO3/d

291

292      return dict(T_design=T, SRT_nit_min=SRTmin, SRT_aer=SRT_aer, SRT_total=SRT, S_eff_bCOD=S,

293                  Px_H=Px_H, Px_D=Px_D, Px_A=Px_A, Px_bio=Px_bio, Px_VSS=Px_VSS, Px_TSS=Px_TSS,

294                  chem_sludge=chem_sludge, Fe_kgd=Fe_kgd, NOx=NOx, NO3_eff=NO3_eff, IR=IR,

295                  NO3_removed=NO3_rem, SDNR_T=SDNR, V_anox=V_anox, V_aer=V_aer, V_bio=V_bio,

296                  f_anox=f_anox, X_mt=X_mt, M_total=M_total, HRT_h=HRT, FM=FM, Y_obs=Y_obs,

297                  VSS_TSS=vss_frac, alk_eff=alk_eff, alk_add_kgd=alk_add)

298

299

300  # ----------------------------------------------------------------------------------

301  # 5. OXYGEN DEMAND & AERATION

302  # ----------------------------------------------------------------------------------

303  def oxygen_demand(inf: Influent, k: Kinetics, bio: dict) -> float:

304      """Average-day actual oxygen requirement AOR, kg O2/d (M&E Eq. 8-17 + denit credit)."""

305      bCOD = inf.bCOD_BOD * inf.BOD

306      Ro = (inf.Q_avg * (bCOD - bio["S_eff_bCOD"]) / 1000 - 1.42 * bio["Px_bio"]

307            + 4.57 * inf.Q_avg * bio["NOx"] / 1000 - 2.86 * bio["NO3_removed"])

308      return Ro

309

310

311  def aeration_design(inf: Influent, d: DesignBasis, m: MembraneSpec, bio: dict, mem: dict,

312                      AOR_avg: float, sub: float | None = None, sote_per_m: float | None = None) -> dict:

313      sub = d.sub_diffuser if sub is None else sub

314      sote_pm = d.sote_per_m if sote_per_m is None else sote_per_m

315      Pb = pressure_at_elev(d.elev_m)

316      res = {}

317      for case, T, pf in (("winter", inf.T_min, 1.0), ("summer", inf.T_max, 1.0),

318                          ("summer max-day", inf.T_max, 1.25)):

319          Cs20 = do_saturation(20)

320          CsT = do_saturation(T) * Pb / P_ATM

321          Pd = Pb + RHO_W * G * sub / 1000

322          CsTH = CsT * 0.5 * (Pd / Pb + 19.0 / 21.0)                    # mid-depth saturation

323          alpha = alpha_factor(d.X_bio)

324          AOR = AOR_avg * pf

325          # O2 delivered by membrane scour air (coarse bubble, in membrane tank)

326          alpha_mt = alpha_factor(bio["X_mt"])

327          sote_sc = m.scour_sote_per_m * m.scour_sub

328          CsTH_mt = CsT * 0.5 * ((Pb + RHO_W * G * m.scour_sub / 1000) / Pb + 19.0 / 21.0)

329          f_mt = alpha_mt * (d.beta * CsTH_mt - 4.0) / Cs20 * 1.024 ** (T - 20)

330          AOTR_scour = mem["air_scour_Nm3h"] * 24 * O2_PER_NM3_AIR * sote_sc * f_mt

331          AOR_proc = max(AOR - AOTR_scour, 0)

332          f_proc = alpha * d.fouling_F * (d.beta * CsTH - d.DO_aer) / Cs20 * 1.024 ** (T - 20)

333          SOTR = AOR_proc / f_proc

334          SOTE = sote_pm * sub

335          air = SOTR / (O2_PER_NM3_AIR * SOTE) / 24                      # Nm3/h

336          res[case] = dict(T=T, alpha=alpha, AOR=AOR, AOTR_scour=AOTR_scour, SOTR=SOTR,

337                           SOTE=SOTE, air_Nm3h=air, AOR_SOR=f_proc)

338      res["design_air_Nm3h"] = max(v["air_Nm3h"] for v in res.values() if isinstance(v, dict))

339      return res

340

341

342  def blower_kW(air_Nm3h: float, submergence: float, losses_kPa: float, eff: float,

343                T_in_C: float = 25.0, elev: float = 120.0) -> float:

344      """Adiabatic blower power, M&E Eq. 5-56 (SI)."""

345      w = air_Nm3h * 1.293 / 3600.0                                     # kg/s

346      p1 = pressure_at_elev(elev)

347      p2 = p1 + RHO_W * G * submergence / 1000 + losses_kPa

348      return w * 8.314 * (T_in_C + 273.15) / (29.7 * 0.283 * eff) * ((p2 / p1) ** 0.283 - 1)

349

350

351  def pump_kW(Q_m3d: float, H: float, eff: float) -> float:

352      return RHO_W * G * (Q_m3d / 86400) * H / eff / 1000

353

354

355  # ----------------------------------------------------------------------------------

356  # 6. ENERGY BALANCE (used for full scale and pilot scale)

357  # ----------------------------------------------------------------------------------

358  def energy_balance(Q: float, air_proc: float, air_scour: float, V_anox: float, R: float, IR: float,

359                     sub_proc: float, sub_scour: float, blower_eff: float, pump_eff: float,

360                     mix_W_m3: float, misc_kWh_m3: float = 0.04) -> dict:

361      kw = dict(

362          process_aeration=blower_kW(air_proc, sub_proc, 15.0, blower_eff),

363          membrane_scour=blower_kW(air_scour, sub_scour, 10.0, blower_eff),

364          permeate_pumping=pump_kW(Q, 6.0, pump_eff),

365          RAS_pumping=pump_kW(R * Q, 1.5, pump_eff * 0.9),

366          MLR_pumping=pump_kW(IR * Q, 0.8, pump_eff * 0.85),

367          anoxic_mixing=V_anox * mix_W_m3 / 1000,

368          screens_CIP_misc=misc_kWh_m3 * Q / 24,

369      )

370      kwh_m3 = {key: v * 24 / Q for key, v in kw.items()}

371      kwh_m3["TOTAL"] = sum(kwh_m3.values())

372      return dict(kW=kw, kWh_m3=kwh_m3)

373

374

375  # ----------------------------------------------------------------------------------

376  # 7. MEMBRANE FOULING / TMP SIMULATION (resistance in series, cleaning regime)

377  # ----------------------------------------------------------------------------------

378  def fouling_simulation(inf: Influent, m: MembraneSpec, mem: dict, days: int = 240, seed: int = 3,

379                         X_mt: float = 11.25):

380      rng = np.random.default_rng(seed)

381      dt = 1.0                                                     # h

382      n = int(days * 24 / dt)

383      t = np.arange(n) * dt / 24.0

384      T = 0.5 * (inf.T_min + inf.T_max) - 0.5 * (inf.T_max - inf.T_min) * np.cos(2 * np.pi * (t - 30) / 365)

385      hour = (np.arange(n) * dt) % 24

386      diurnal = 1 + 0.38 * np.sin(2 * np.pi * (hour - 9) / 24) + rng.normal(0, 0.05, n)

387      storms = np.zeros(n)

388      for d0 in rng.choice(np.arange(5, days - 2), size=6, replace=False):   # wet-weather events

389          i0 = int(d0 * 24); storms[i0:i0 + 18] = 0.55

390      Qh = inf.Q_avg / 24 * np.clip(diurnal + storms, 0.4, inf.pf_peakhour)

391

392      Rm = 1 / (water_viscosity(20) * m.Lp_clean20 / 3.6e6 / 1e5)

393      J_ref = m.J_avg20 / 3.6e6

394      k_res, f_irr, f_irremov = 4.0e11, 0.42, 0.006        # m^-1 per (m3/m2), fractions

395      # fouling propensity falls with scour intensity and rises with mixed-liquor solids

396      # (empirical exponents in the range reported for HF MBRs; =1 at SAD_m 0.25, MLSS 11.25)

397      k_res *= (0.25 / m.SAD_m) ** 0.8 * (X_mt / 11.25) ** 0.5

398      Rres = Rirr = Rperm = 0.0

399      TMP = np.zeros(n); J = np.zeros(n); Lp = np.zeros(n); events = []

400      A_on = mem["A_installed"]

401      offline_until = -1

402      for i in range(n):

403          A = A_on * (m.n_trains - 1) / m.n_trains if i < offline_until else A_on

404          Jg = Qh[i] * 1000 / (A * mem["availability"]) / 3.6e6       # m/s gross

405          mu = water_viscosity(T[i])

406          dV = Jg * 3600 * dt                                          # m3/m2 filtered

407          dR = k_res * (Jg / J_ref) ** 2 * dV

408          Rres += dR; Rirr += f_irr * dR; Rperm += f_irremov * dR

409          TMP[i] = mu * Jg * (Rm + Rres + Rirr + Rperm) / 1e5          # bar

410          J[i] = Jg * 3.6e6

411          Lp[i] = J[i] / TMP[i] * (water_viscosity(T[i]) / water_viscosity(20))

412          if i % (7 * 24) == 0 and i > 0:                               # weekly maintenance clean

413              Rres *= 0.25; events.append((t[i], "MC"))

414          if TMP[i] > m.TMP_max:                                        # recovery clean (CIP)

415              Rres, Rirr = 0.0, Rirr * 0.08

416              offline_until = i + 12

417              events.append((t[i], "RC"))

418      return dict(t=t, T=T, J=J, TMP=TMP, Lp=Lp, events=events)

419

420

421  # ----------------------------------------------------------------------------------

422  # 8. RETROFIT (MODERNIZATION) CAPACITY CHECK

423  # ----------------------------------------------------------------------------------

424  def retrofit_check(inf: Influent, d: DesignBasis, bio: dict, mem: dict, cas: ExistingCAS,

425                     m: MembraneSpec) -> dict:

426      V_exist = cas.n_aer_tanks * cas.V_aer_each

427      px_per_m3 = bio["Px_TSS"] / inf.Q_avg                         # kg TSS / m3 treated

428      Qmax_cas = V_exist * cas.X_cas / (px_per_m3 * bio["SRT_total"])

429      Qmax_mbr = (V_exist * d.X_bio + mem["V_mt"] * bio["X_mt"]) / (px_per_m3 * bio["SRT_total"])

430      clar_area = cas.n_clarifiers * math.pi * cas.clarifier_D**2 / 4

431      clar_vol = clar_area * cas.clarifier_swd

432      return dict(X_cas=cas.X_cas, X_mbr=d.X_bio, V_existing=V_exist, V_mbr_required=bio["V_bio"], fits=bio["V_bio"] <= V_exist,

433                  Qmax_CAS=Qmax_cas, Qmax_MBR=Qmax_mbr, capacity_gain=Qmax_mbr / Qmax_cas,

434                  freed_volume=V_exist - bio["V_bio"], clarifier_area_released=clar_area,

435                  clarifier_volume_released=clar_vol,

436                  MT_footprint=mem["L_train"] * mem["W_train"] * m.n_trains)

437

438

439  # ----------------------------------------------------------------------------------

440  # 9. SCALE-UP: pilot (1 module)  ->  cassette  ->  train  ->  full plant

441  # ----------------------------------------------------------------------------------

442  def scale_up(inf: Influent, d: DesignBasis, k: Kinetics, m: MembraneSpec, mem: dict,

443               bio: dict, aer: dict, AOR: float) -> dict:

444      """Modular 'numbering-up' of membranes + similarity-based scale-up of biology/aeration.

445      Scale-invariant (kept constant): flux, SAD_m, SRT, MLSS, HRT, F/M, R, IR, cleaning

446      protocol (chemical dose per m2), filtration/relax cycle, fibre packing.

447      Scale-variant (recomputed): diffuser submergence -> SOTE, blower/pump efficiency,

448      mixing power density, hydraulic distribution between cassettes, diurnal peaking."""

449      Q_full = inf.Q_avg

450      Q_pilot = m.module_area * mem["J_operating_avg"] * mem["availability"] * 24 / 1000

451      S = Q_full / Q_pilot

452

453      V_bio_p = bio["V_bio"] / S

454      V_anox_p = bio["V_anox"] / S

455      sub_pilot = 2.2

456      aer_p = aeration_design(inf, d, m, bio, {**mem, "air_scour_Nm3h": m.module_area * m.SAD_m},

457                              AOR / S, sub=sub_pilot)

458      air_scour_p = m.module_area * m.SAD_m

459

460      E_full = energy_balance(Q_full, aer["design_air_Nm3h"] / 1.25 * 1.0, mem["air_scour_Nm3h"],

461                              bio["V_anox"], d.R_ras, bio["IR"], d.sub_diffuser, m.scour_sub,

462                              blower_eff=0.75, pump_eff=0.70, mix_W_m3=d.anox_mix_W_m3)

463      E_pilot = energy_balance(Q_pilot, aer_p["design_air_Nm3h"] / 1.25, air_scour_p,

464                               V_anox_p, d.R_ras, bio["IR"], sub_pilot, 2.0,

465                               blower_eff=0.45, pump_eff=0.40, mix_W_m3=15.0, misc_kWh_m3=0.10)

466

467      # Hydraulic maldistribution between cassettes at full scale (manifold headloss criterion)

468      # keep permeate manifold headloss < 10 % of TMP -> flux non-uniformity < ~5 %

469      n_c = mem["n_cas_train"]

470      maldist = 1 + 0.012 * n_c                     # empirical: peak-cassette flux factor

471

472      levels = [

473          ("Pilot\n(1 module)", 1, m.module_area, Q_pilot),

474          ("Cassette", m.modules_per_cassette, mem["A_cassette"], Q_pilot * m.modules_per_cassette),

475          ("Train", m.modules_per_cassette * n_c, mem["A_cassette"] * n_c,

476           Q_pilot * m.modules_per_cassette * n_c),

477          ("Full plant", mem["n_modules"], mem["A_installed"], Q_pilot * mem["n_modules"]),

478      ]

479      invariants = {

480          "Gross flux (L/m2.h)": mem["J_operating_avg"],

481          "SAD_m (Nm3/m2.h)": m.SAD_m,

482          "SAD_p (Nm3/m3)": mem["SAD_p"],

483          "SRT total (d)": bio["SRT_total"],

484          "MLSS bio / MT (g/L)": f'{d.X_bio:.1f} / {bio["X_mt"]:.2f}',

485          "HRT (h)": bio["HRT_h"],

486          "F/M (kg BOD/kg VSS.d)": bio["FM"],

487          "Recycles R / IR": f'{d.R_ras:.1f} / {bio["IR"]:.1f}',

488          "Filtration/relax (min)": f"{m.t_filt:.0f} / {m.t_relax:.0f}",

489      }

490      variants = {

491          "Diffuser submergence (m)": (sub_pilot, d.sub_diffuser),

492          "Process SOTE (%)": (aer_p["summer max-day"]["SOTE"] * 100, aer["summer max-day"]["SOTE"] * 100),

493          "Process air (Nm3/m3)": (aer_p["design_air_Nm3h"] / 1.25 * 24 / Q_pilot,

494                                    aer["design_air_Nm3h"] / 1.25 * 24 / Q_full),

495          "Blower efficiency (-)": (0.45, 0.75),

496          "Mixing (W/m3)": (15.0, d.anox_mix_W_m3),

497          "Peak-cassette flux factor": (1.0, maldist),

498          "Specific energy (kWh/m3)": (E_pilot["kWh_m3"]["TOTAL"], E_full["kWh_m3"]["TOTAL"]),

499      }

500      return dict(Q_pilot=Q_pilot, scale_factor=S, V_bio_pilot=V_bio_p, levels=levels,

501                  invariants=invariants, variants=variants, E_full=E_full, E_pilot=E_pilot)

502

503

504  # ----------------------------------------------------------------------------------

505  # 10. DIAGRAMS

506  # ----------------------------------------------------------------------------------

507  C_TANK = "#dceefb"; C_EDGE = "#1f4e79"; C_AIR = "#2e8b57"; C_SLUDGE = "#8b5a2b"

508  C_REC = "#c0392b"; C_PERM = "#1565c0"; C_CHEM = "#7b3fa0"

509

510

511  def _box(ax, x, y, w, h, title, sub="", fc="#eef4fa", ec=C_EDGE, fs=9.5):

512      ax.add_patch(FancyBboxPatch((x, y), w, h, boxstyle="round,pad=0.02,rounding_size=0.12",

513                                  fc=fc, ec=ec, lw=1.6))

514      ax.text(x + w / 2, y + h - 0.15, title, ha="center", va="top", fontsize=fs, weight="bold",

515              color="#0f2236")

516      if sub:

517          ax.text(x + w / 2, y + (h - 0.45) / 2, sub, ha="center", va="center", fontsize=fs - 2,

518                  color="#222", linespacing=1.35)

519

520

521  def _arrow(ax, pts, color=C_EDGE, lw=2.0, ls="-", head=True):

522      xs, ys = zip(*pts)

523      ax.plot(xs[:-1] + (xs[-1],), ys[:-1] + (ys[-1],), color=color, lw=lw, ls=ls,

524              solid_capstyle="round", zorder=1)

525      if head:

526          ax.annotate("", xy=pts[-1], xytext=pts[-2],

527                      arrowprops=dict(arrowstyle="-|>", color=color, lw=lw, mutation_scale=16), zorder=2)

528

529

530  def _tank(ax, x, y, w, h, title, lines, fc=C_TANK):

531      ax.add_patch(Rectangle((x, y), w, h, fc=fc, ec=C_EDGE, lw=2.0))

532      ax.plot([x, x + w], [y + h * 0.88] * 2, color="#5dade2", lw=1.2, ls=(0, (6, 3)))

533      ax.text(x + w / 2, y + h - 0.12, title, ha="center", va="top", fontsize=10, weight="bold",

534              color="#0f2236")

535      ax.text(x + w / 2, y + h * 0.48, lines, ha="center", va="center", fontsize=7.6,

536              linespacing=1.35, color="#1b1b1b")

537

538

539  def draw_pfd(inf, d, m, mem, bio, aer, fname):

540      fig, ax = plt.subplots(figsize=(19, 9.5))

541      ax.set_xlim(0, 33); ax.set_ylim(0, 14); ax.axis("off")

542      Qa = inf.Q_avg

543

544      ax.text(16.5, 13.6, "MBR Modernization - Process Flow Diagram (MLE-MBR, submerged hollow-fibre)",

545              ha="center", fontsize=15, weight="bold", color="#0f2236")

546      ax.text(16.5, 13.05, f"Q_avg = {Qa:,.0f} m³/d   |   Q_peak-hour = {Qa*inf.pf_peakhour:,.0f} m³/d   |   "

547              f"Winter design T = {inf.T_min:.0f} °C   |   Effluent: NH₄-N ≤ {d.NH4_eff:.0f}, TN ≤ {d.TN_eff:.0f}, "

548              f"TP ≤ {d.TP_eff} mg/L, TSS < 1 mg/L", ha="center", fontsize=9.5, color="#333")

549

550      # Pretreatment

551      _arrow(ax, [(0.1, 8.0), (1.0, 8.0)]); ax.text(0.1, 8.25, "Raw\nWW", fontsize=8.5, weight="bold")

552      _box(ax, 1.0, 7.0, 2.3, 2.0, "Coarse\nscreen", "6 mm bar\nscreen")

553      _arrow(ax, [(3.3, 8.0), (3.8, 8.0)])

554      _box(ax, 3.8, 7.0, 2.4, 2.0, "Grit &\ngrease", "aerated\ngrit chamber")

555      _arrow(ax, [(6.2, 8.0), (6.7, 8.0)])

556      _box(ax, 6.7, 7.0, 2.5, 2.0, "Fine\nscreen", "≤1 mm punched\nplate (fibre\nprotection)", fc="#fff4e0")

557      _arrow(ax, [(9.2, 8.0), (10.0, 8.0)])

558

559      # Bioreactors

560      _tank(ax, 10.0, 6.0, 4.4, 3.6, "ANOXIC",

561            f"V = {bio['V_anox']:,.0f} m³\nMLSS {d.X_bio:.1f} g/L\nSDNR {bio['SDNR_T']:.3f} gN/gVSS·d\n"

562            f"NO₃ removed {bio['NO3_removed']:,.0f} kg/d\nmixers {d.anox_mix_W_m3:.0f} W/m³")

563      _tank(ax, 14.4, 6.0, 6.4, 3.6, "AEROBIC (nitrification)",

564            f"V = {bio['V_aer']:,.0f} m³   SWD {d.swd_bio} m\nSRT_aer {bio['SRT_aer']:.1f} d / SRT_tot {bio['SRT_total']:.1f} d\n"

565            f"DO {d.DO_aer} mg/L   α = {aer['winter']['alpha']:.2f}\n"

566            f"AOR {aer['summer max-day']['AOR']:,.0f} kg O₂/d (max-day)")

567      for xx in np.arange(14.8, 20.6, 0.45):  # fine-bubble diffusers

568          ax.add_patch(Circle((xx, 6.25), 0.07, color=C_AIR))

569      for xx in (11.2, 13.2):                  # mixers

570          ax.plot([xx, xx], [6.4, 7.0], color="#555", lw=1.5); ax.plot([xx - .25, xx + .25], [6.45, 6.35], color="#555", lw=2)

571

572      _arrow(ax, [(20.8, 7.4), (21.6, 7.4)])

573      ax.text(21.2, 7.6, f"{1+d.R_ras:.0f}Q", ha="center", fontsize=8, color=C_EDGE)

574

575      # Membrane tank

576      _tank(ax, 21.6, 6.0, 4.8, 3.6, f"MEMBRANE TANKS ×{m.n_trains}", "", fc="#e6f5ec")

577      for j in range(4):

578          x0 = 22.0 + j * 1.05

579          ax.add_patch(Rectangle((x0, 6.55), 0.75, 1.6, fc="white", ec="#2c3e50", lw=1))

580          for f in np.linspace(x0 + 0.1, x0 + 0.65, 6):

581              ax.plot([f, f], [6.6, 8.1], color="#7f8c8d", lw=0.6)

582      ax.text(24.0, 8.55, f"{mem['n_cassettes']} cassettes · {mem['A_installed']:,.0f} m²\n"

583              f"J_avg {mem['J_operating_avg']:.1f} LMH · MLSS {bio['X_mt']:.1f} g/L",

584              ha="center", va="center", fontsize=7.4, linespacing=1.3)

585

586      # Permeate

587      _arrow(ax, [(26.4, 8.6), (27.0, 8.6)], color=C_PERM)

588      _box(ax, 27.0, 7.6, 2.4, 2.0, "Permeate\npumps", f"VFD, {m.t_filt:.0f}/{m.t_relax:.0f} min\nfilt./relax\nTMP ≤ {m.TMP_max} bar", fc="#e3f0ff", ec=C_PERM)

589      _arrow(ax, [(29.4, 8.6), (30.0, 8.6)], color=C_PERM)

590      _box(ax, 30.0, 7.6, 2.6, 2.0, "UV / reuse", "Effluent\nTSS<1, turb.<0.2 NTU\nBOD<3 mg/L", fc="#e3f0ff", ec=C_PERM)

591

592      # RAS: membrane tank -> aerobic (above)

593      _arrow(ax, [(24.0, 9.6), (24.0, 11.4), (19.6, 11.4), (19.6, 9.6)], color=C_REC, lw=2.2)

594      ax.text(21.8, 11.6, f"RAS  R = {d.R_ras:.0f}Q  ({d.R_ras*Qa:,.0f} m³/d)", ha="center", fontsize=8.5, color=C_REC, weight="bold")

595      # MLR: aerobic -> anoxic

596      _arrow(ax, [(17.0, 9.6), (17.0, 10.5), (12.2, 10.5), (12.2, 9.6)], color=C_REC, lw=2.2, ls=(0, (5, 2)))

597      ax.text(14.6, 10.7, f"MLR (nitrate)  IR = {bio['IR']:.1f}Q", ha="center", fontsize=8.5, color=C_REC, weight="bold")

598

599      # Blowers / air

600      _box(ax, 15.8, 1.2, 3.4, 1.8, "Process blowers", f"{aer['design_air_Nm3h']:,.0f} Nm³/h (max-day)\nturbo, DO-cascade control", fc="#eaf7ef", ec=C_AIR)

601      _arrow(ax, [(17.5, 3.0), (17.5, 6.0)], color=C_AIR)

602      _box(ax, 21.6, 1.2, 3.4, 1.8, "Scour blowers", f"{mem['air_scour_Nm3h']:,.0f} Nm³/h\nSAD_m {m.SAD_m} Nm³/m²·h", fc="#eaf7ef", ec=C_AIR)

603      _arrow(ax, [(23.3, 3.0), (23.3, 6.0)], color=C_AIR)

604

605      # WAS / sludge

606      _arrow(ax, [(25.8, 6.0), (25.8, 3.6), (27.0, 3.6)], color=C_SLUDGE)

607      _box(ax, 27.0, 2.6, 3.6, 2.0, "Sludge line", f"WAS {bio['Px_TSS']:,.0f} kg TSS/d\n"

608           f"≈{bio['Px_TSS']/bio['X_mt']:,.0f} m³/d → thickening\n→ dewatering", fc="#f6ece2", ec=C_SLUDGE)

609

610      # Chemicals

611      _box(ax, 27.0, 10.8, 3.6, 1.8, "CIP / dosing", "NaOCl 500-1000 ppm (MC/RC)\nCitric acid 2000 ppm\n"

612           f"FeCl₃ {bio['Fe_kgd']:,.0f} kg Fe/d (P)", fc="#f3eafa", ec=C_CHEM)

613      _arrow(ax, [(27.0, 11.2), (26.0, 11.2), (26.0, 9.6)], color=C_CHEM, ls=(0, (3, 2)))

614      _arrow(ax, [(28.8, 10.8), (28.8, 10.2), (15.5, 10.2), (15.5, 9.6)], color=C_CHEM, ls=(0, (1, 2)), lw=1.4)

615

616      # Legend

617      ly = 4.6

618      for i, (c, lab, ls) in enumerate([(C_EDGE, "Mixed liquor / wastewater", "-"), (C_PERM, "Permeate", "-"),

619                                        (C_REC, "Recycles", "-"), (C_AIR, "Air", "-"),

620                                        (C_SLUDGE, "Waste sludge", "-"), (C_CHEM, "Chemicals", ":")]):

621          ax.plot([0.5, 1.4], [ly - i * 0.55] * 2, color=c, lw=2.2, ls=ls)

622          ax.text(1.6, ly - i * 0.55, lab, va="center", fontsize=8.5)

623      ax.text(0.5, 5.2, "Legend", weight="bold", fontsize=9.5)

624

625      ax.text(5.0, 4.6, f"Total bioreactor volume {bio['V_bio']:,.0f} m³  +  membrane tanks {mem['V_mt']:,.0f} m³\n"

626              f"HRT {bio['HRT_h']:.1f} h  ·  F/M {bio['FM']:.3f} kg BOD/kg VSS·d  ·  Y_obs {bio['Y_obs']:.2f} kg TSS/kg BOD\n"

627              f"Anoxic fraction {bio['f_anox']*100:.0f} %  ·  NOx formed {bio['NOx']:.1f} mg N/L\n"

628              f"Membrane area governed by: {mem['governing']}",

629              fontsize=9, va="top", linespacing=1.5,

630              bbox=dict(boxstyle="round", fc="#fbfbfb", ec="#999"))

631      fig.savefig(fname, dpi=170, bbox_inches="tight"); plt.close(fig)

632

633

634  def draw_scaleup(sc, m, fname):

635      fig = plt.figure(figsize=(18, 10))

636      ax = fig.add_axes([0.02, 0.48, 0.96, 0.48]); ax.axis("off"); ax.set_xlim(0, 32); ax.set_ylim(0, 9)

637      ax.text(16, 8.6, "Scale-up strategy: modular numbering-up of membranes + similarity scale-up of biology",

638              ha="center", fontsize=14, weight="bold")

639      xs = [0.8, 8.8, 16.8, 24.8]

640      mults = [f"×{m.modules_per_cassette}", f"×{sc['levels'][2][1]//m.modules_per_cassette}",

641               f"×{sc['levels'][3][1]//sc['levels'][2][1]}"]

642      for i, ((lab, nmod, A, Q), x) in enumerate(zip(sc["levels"], xs)):

643          _box(ax, x, 2.6, 6.4, 5.2, lab.replace("\n", " "),

644               f"{nmod:,} module(s)\nArea {A:,.0f} m²\nQ ≈ {Q:,.1f} m³/d\n"

645               f"scale factor {Q/sc['Q_pilot']:,.0f}×", fc=["#fff4e0", "#eef4fa", "#e6f5ec", "#e3f0ff"][i], fs=12)

646          # small icon of modules

647          nshow = min(nmod, 24)

648          cols = 12

649          for j in range(nshow):

650              r, c = divmod(j, cols)

651              ax.add_patch(Rectangle((x + 0.45 + c * 0.47, 2.85 + r * 0.55), 0.35, 0.45, fc="white", ec="#555", lw=.6))

652          if i < 3:

653              _arrow(ax, [(x + 6.5, 5.2), (xs[i + 1] - 0.1, 5.2)], lw=2.5)

654              ax.text((x + 6.5 + xs[i + 1]) / 2, 5.5, mults[i], ha="center", fontsize=12, weight="bold", color=C_REC)

655      ax.text(16, 1.6, "Kept constant across scales (scale-invariant):  " +

656              "  ·  ".join(f"{k}: {v:.3g}" if isinstance(v, float) else f"{k}: {v}" for k, v in list(sc["invariants"].items())[:5]),

657              ha="center", fontsize=9)

658      ax.text(16, 0.9, "  ·  ".join(f"{k}: {v:.3g}" if isinstance(v, float) else f"{k}: {v}" for k, v in list(sc["invariants"].items())[5:]),

659              ha="center", fontsize=9)

660

661      # Bottom left: energy breakdown pilot vs full

662      ax2 = fig.add_axes([0.06, 0.06, 0.42, 0.34])

663      keys = [k for k in sc["E_full"]["kWh_m3"] if k != "TOTAL"]

664      pil = [sc["E_pilot"]["kWh_m3"][k] for k in keys]; ful = [sc["E_full"]["kWh_m3"][k] for k in keys]

665      bottom_p = bottom_f = 0

666      cmap = plt.get_cmap("tab10")

667      for i, k in enumerate(keys):

668          ax2.bar(0, pil[i], bottom=bottom_p, color=cmap(i), width=0.55, label=k.replace("_", " "))

669          ax2.bar(1, ful[i], bottom=bottom_f, color=cmap(i), width=0.55)

670          bottom_p += pil[i]; bottom_f += ful[i]

671      ax2.set_xticks([0, 1]); ax2.set_xticklabels([f"Pilot\n({sc['Q_pilot']:.1f} m³/d)", f"Full scale\n({sc['Q_pilot']*sc['scale_factor']:,.0f} m³/d)"])

672      ax2.text(0, bottom_p + 0.03, f"{bottom_p:.2f}", ha="center", weight="bold")

673      ax2.text(1, bottom_f + 0.03, f"{bottom_f:.2f}", ha="center", weight="bold")

674      ax2.set_ylabel("Specific energy, kWh/m³ permeate"); ax2.set_title("Energy demand: pilot vs full scale")

675      ax2.legend(fontsize=7.5, loc="upper right"); ax2.grid(axis="y", alpha=.3)

676

677      # Bottom right: scale-variant parameter table

678      ax3 = fig.add_axes([0.54, 0.06, 0.43, 0.34]); ax3.axis("off")

679      rows = [[k, f"{v[0]:.3g}", f"{v[1]:.3g}"] for k, v in sc["variants"].items()]

680      tb = ax3.table(cellText=rows, colLabels=["Scale-variant parameter", "Pilot", "Full scale"],

681                     loc="center", cellLoc="center", colWidths=[0.55, 0.2, 0.2])

682      tb.auto_set_font_size(False); tb.set_fontsize(9.5); tb.scale(1, 1.6)

683      for (r, c), cell in tb.get_celld().items():

684          if r == 0: cell.set_facecolor("#1f4e79"); cell.set_text_props(color="white", weight="bold")

685      ax3.set_title("What changes on scale-up (must be corrected, not copied)", fontsize=11)

686      fig.savefig(fname, dpi=160, bbox_inches="tight"); plt.close(fig)

687

688

689  def plot_fouling(sim, m, fname):

690      fig, axs = plt.subplots(3, 1, figsize=(14, 9.5), sharex=True)

691      t = sim["t"]

692      axs[0].plot(t, sim["J"], lw=0.4, color=C_PERM); axs[0].set_ylabel("Gross flux\n(L/m²·h)")

693      ax0b = axs[0].twinx(); ax0b.plot(t, sim["T"], color="#e67e22", lw=1.5); ax0b.set_ylabel("T (°C)", color="#e67e22")

694      axs[1].plot(t, sim["TMP"], lw=0.5, color="#c0392b"); axs[1].axhline(m.TMP_max, ls="--", color="k", lw=1)

695      axs[1].text(t[-1], m.TMP_max + 0.005, "recovery-clean trigger", ha="right", fontsize=8)

696      axs[1].set_ylabel("TMP (bar)")

697      axs[2].plot(t, sim["Lp"], lw=0.5, color=C_AIR); axs[2].set_ylabel("Permeability\n@20°C (LMH/bar)")

698      axs[2].set_xlabel("Operating time (days)")

699      for tt, ev in sim["events"]:

700          if ev == "RC":

701              for a in axs[1:]:

702                  a.axvline(tt, color="#7b3fa0", lw=1.2, alpha=.7)

703      axs[1].plot([], [], color="#7b3fa0", label="Recovery clean (CIP)"); axs[1].legend(loc="upper left", fontsize=8)

704      axs[0].set_title("Membrane performance simulation: diurnal & storm flows, seasonal temperature, weekly maintenance cleans")

705      for a in axs: a.grid(alpha=.3)

706      fig.tight_layout(); fig.savefig(fname, dpi=160); plt.close(fig)

707

708

709  def plot_sensitivity(inf, d, k, m, fname):

710      fig, axs = plt.subplots(1, 2, figsize=(15, 5.6))

711      # (a) membrane area vs design temperature for several design fluxes

712      Ts = np.linspace(8, 24, 33)

713      for J in (20, 25, 30, 35):

714          A = []

715          for T in Ts:

716              i2 = Influent(**{**asdict(inf), "T_min": T}); m2 = MembraneSpec(**{**asdict(m), "J_avg20": J, "J_mm20": J * 1.2, "J_peak20": J * 1.6})

717              A.append(membrane_design(i2, m2)["A_installed"] / 1000)

718          axs[0].plot(Ts, A, lw=2, label=f"J_avg,20 = {J} LMH")

719      axs[0].set_xlabel("Winter design temperature (°C)"); axs[0].set_ylabel("Installed membrane area (×1000 m²)")

720      axs[0].set_title("(a) Membrane area sensitivity (viscosity-corrected flux)"); axs[0].legend(); axs[0].grid(alpha=.3)

721

722      # (b) MLSS optimisation: volume decreases, alpha penalty increases air

723      Xs = np.linspace(5, 14, 28); V, AIR = [], []

724      for X in Xs:

725          d2 = DesignBasis(**{**asdict(d), "X_bio": X})

726          mem = membrane_design(inf, m); bio = biological_design(inf, d2, k, mem)

727          aer = aeration_design(inf, d2, m, bio, mem, oxygen_demand(inf, k, bio))

728          V.append(bio["V_bio"]); AIR.append(aer["design_air_Nm3h"])

729      axs[1].plot(Xs, V, color=C_EDGE, lw=2.2, label="Bioreactor volume")

730      axs[1].set_xlabel("Bioreactor MLSS (g/L)"); axs[1].set_ylabel("Volume (m³)", color=C_EDGE)

731      b = axs[1].twinx(); b.plot(Xs, AIR, color=C_AIR, lw=2.2, label="Process air (max-day)")

732      b.set_ylabel("Process air (Nm³/h)", color=C_AIR)

733      axs[1].axvspan(8, 12, color="#f9e79f", alpha=.35); axs[1].text(10, max(V) * 0.95, "typical MBR\nwindow", ha="center", fontsize=9)

734      axs[1].set_title("(b) MLSS trade-off: footprint vs α-factor aeration penalty"); axs[1].grid(alpha=.3)

735      fig.tight_layout(); fig.savefig(fname, dpi=160); plt.close(fig)

736

737

738  def plot_retrofit(rf, fname):

739      fig, axs = plt.subplots(1, 2, figsize=(13, 5))

740      axs[0].bar([f"Existing CAS\n(MLSS {rf['X_cas']} g/L)", f"MBR in same tanks\n(MLSS {rf['X_mbr']} g/L)"], [rf["Qmax_CAS"], rf["Qmax_MBR"]],

741                 color=["#95a5a6", C_EDGE], width=.55)

742      for i, v in enumerate([rf["Qmax_CAS"], rf["Qmax_MBR"]]):

743          axs[0].text(i, v * 1.01, f"{v:,.0f} m³/d", ha="center", weight="bold")

744      axs[0].set_ylabel("Treatment capacity at same SRT & nutrient targets (m³/d)")

745      axs[0].set_title(f"Capacity gain ×{rf['capacity_gain']:.2f} without new bioreactor volume")

746      axs[1].bar(["Existing aeration\nvolume", "MBR bio volume\nrequired"], [rf["V_existing"], rf["V_mbr_required"]],

747                 color=["#95a5a6", C_AIR], width=.55)

748      axs[1].set_ylabel("m³"); axs[1].set_title(f"Freed volume {rf['freed_volume']:,.0f} m³ · clarifiers ({rf['clarifier_area_released']:,.0f} m²) released")

749      for a in axs: a.grid(axis="y", alpha=.3)

750      fig.tight_layout(); fig.savefig(fname, dpi=160); plt.close(fig)

751

752

753  # ----------------------------------------------------------------------------------

754  # 11. MAIN

755  # ----------------------------------------------------------------------------------

756  def main():

757      inf, d, k, m, cas = Influent(), DesignBasis(), Kinetics(), MembraneSpec(), ExistingCAS()

758

759      mem = membrane_design(inf, m)

760      bio = biological_design(inf, d, k, mem)

761      AOR = oxygen_demand(inf, k, bio)

762      aer = aeration_design(inf, d, m, bio, mem, AOR)

763      rf = retrofit_check(inf, d, bio, mem, cas, m)

764      sc = scale_up(inf, d, k, m, mem, bio, aer, AOR)

765      sim = fouling_simulation(inf, m, mem, X_mt=bio["X_mt"])

766

767      draw_pfd(inf, d, m, mem, bio, aer, f"{OUT}/01_process_flow_diagram.png")

768      draw_scaleup(sc, m, f"{OUT}/02_scale_up_strategy.png")

769      plot_fouling(sim, m, f"{OUT}/03_membrane_fouling_TMP.png")

770      plot_sensitivity(inf, d, k, m, f"{OUT}/04_design_sensitivity.png")

771      plot_retrofit(rf, f"{OUT}/05_retrofit_capacity.png")

772

773      n_rc = sum(1 for _, e in sim["events"] if e == "RC")

774      E = sc["E_full"]["kWh_m3"]

775      lines = [

776          "# MBR Preliminary Design Report (auto-generated by mbr_design.py)\n",

777          f"Design flow {inf.Q_avg:,.0f} m³/d avg, {inf.Q_avg*inf.pf_peakhour:,.0f} m³/d peak hour; winter {inf.T_min} °C.\n",

778          "## Biological process (MLE)",

779          f"- Min. nitrification SRT at {inf.T_min} °C: {bio['SRT_nit_min']:.1f} d → aerobic SRT {bio['SRT_aer']:.1f} d, total SRT {bio['SRT_total']:.1f} d",

780          f"- Anoxic {bio['V_anox']:,.0f} m³ + aerobic {bio['V_aer']:,.0f} m³ = {bio['V_bio']:,.0f} m³ (anoxic fraction {bio['f_anox']*100:.0f} %)",

781          f"- MLSS bio/membrane tank: {d.X_bio:.1f} / {bio['X_mt']:.2f} g/L; HRT {bio['HRT_h']:.1f} h; F/M {bio['FM']:.3f}",

782          f"- Sludge production {bio['Px_TSS']:,.0f} kg TSS/d (incl. {bio['chem_sludge']:,.0f} kg/d chemical); Y_obs {bio['Y_obs']:.2f} kg TSS/kg BOD",

783          f"- NOx formed {bio['NOx']:.1f} mg/L, internal recycle IR = {bio['IR']:.2f}Q, NO₃ removed {bio['NO3_removed']:,.0f} kg N/d",

784          f"- FeCl₃ for TP {d.TP_eff} mg/L: {bio['Fe_kgd']:,.0f} kg Fe/d; residual alkalinity {bio['alk_eff']:.0f} mg/L CaCO₃ (supplement {bio['alk_add_kgd']:,.0f} kg/d)",

785          "\n## Membranes",

786          f"- Flux viscosity correction at {inf.T_min} °C: ×{mem['mu_ratio']:.3f}; availability {mem['availability']*100:.1f} %",

787          f"- Area required: avg N-1 = {mem['A_avg']:,.0f} m², max-month = {mem['A_mm']:,.0f} m², peak-hour = {mem['A_ph']:,.0f} m² → governed by {mem['governing']}",

788          f"- Installed: {m.n_trains} trains × {mem['n_cas_train']} cassettes = {mem['n_cassettes']} cassettes, {mem['n_modules']:,} modules, {mem['A_installed']:,.0f} m²",

789          f"- Operating avg gross flux {mem['J_operating_avg']:.1f} LMH; SAD_m {m.SAD_m} → scour air {mem['air_scour_Nm3h']:,.0f} Nm³/h; SAD_p {mem['SAD_p']:.1f} Nm³/m³",

790          f"- Membrane tank volume {mem['V_mt']:,.0f} m³ (train {mem['L_train']:.1f} × {mem['W_train']:.1f} × {m.mt_depth} m); packing {mem['packing_density']:.0f} m²/m³",

791          f"- 240-day simulation: {n_rc} recovery cleans (TMP > {m.TMP_max} bar), weekly maintenance cleans",

792          "\n## Aeration",

793          *[f"- {c}: α={aer[c]['alpha']:.2f}, AOR {aer[c]['AOR']:,.0f} kg/d, scour-air O₂ credit {aer[c]['AOTR_scour']:,.0f} kg/d, "

794            f"SOTR {aer[c]['SOTR']:,.0f} kg/d, air {aer[c]['air_Nm3h']:,.0f} Nm³/h" for c in ("winter", "summer", "summer max-day")],

795          "\n## Energy (full scale, average day)",

796          *[f"- {k_}: {v:.3f} kWh/m³" for k_, v in E.items()],

797          "\n## Modernization (retrofit) check",

798          f"- Existing aeration volume {rf['V_existing']:,.0f} m³ vs MBR bio volume {rf['V_mbr_required']:,.0f} m³ → fits: {rf['fits']}",

799          f"- Capacity of existing tanks: CAS {rf['Qmax_CAS']:,.0f} m³/d → MBR {rf['Qmax_MBR']:,.0f} m³/d (×{rf['capacity_gain']:.2f})",

800          f"- Secondary clarifiers released ({rf['clarifier_volume_released']:,.0f} m³) → membrane tanks / EQ / sludge storage",

801          "\n## Scale-up (pilot → full)",

802          f"- Pilot = 1 module ({m.module_area} m²) treating {sc['Q_pilot']:.1f} m³/d; scale factor {sc['scale_factor']:,.0f}×",

803          *[f"- invariant · {k_}: {v:.3g}" if isinstance(v, float) else f"- invariant · {k_}: {v}" for k_, v in sc["invariants"].items()],

804          *[f"- variant · {k_}: pilot {v[0]:.3g} → full {v[1]:.3g}" for k_, v in sc["variants"].items()],

805      ]

806      with open(f"{OUT}/design_report.md", "w") as fh:

807          fh.write("\n".join(lines))

808      with open(f"{OUT}/design_results.json", "w") as fh:

809          json.dump(dict(membrane=mem, biology=bio, aeration=aer, retrofit=rf,

810                         energy_full=sc["E_full"], energy_pilot=sc["E_pilot"]), fh, indent=2, default=str)

811      print("\n".join(lines))

812

813

814  if __name__ == "__main__":

815      main()

816

# Appendix B. doe_runner.py: DOE, response surfaces and JSL generator

Requires mbr_design.py in the same folder. Run with: python doe_runner.py.

1  #!/usr/bin/env python3

2  """

3  =====================================================================================

4   DOE RUNNER for the MBR preliminary-design model (mbr_design.py)

5  -------------------------------------------------------------------------------------

6   1. Builds a face-centred Central Composite Design (CCD, alpha = 1) in 5 factors:

7          MLSS_gL     bioreactor MLSS               7 - 11  g/L

8          Flux20_LMH  gross design flux @20 degC   20 - 30  L/m2.h

9          SADm        membrane scour air demand   0.15 - 0.35 Nm3/m2.h

10          Tmin_C      winter design temperature    10 - 16  degC   (noise / climate factor)

11          SRTaer_d    aerobic SRT floor            12 - 20  d

12      32 factorial + 10 axial + 6 centre points = 48 runs, randomised run order

13      (identical structure to JMP: DOE > Classical > Response Surface Design > CCD-Uniform/Face).

14   2. Runs the full engineering model at every point (biology, membranes, aeration,

15      energy and the 240-day fouling simulation).

16   3. Writes  mbr_doe_runs.csv        -> open in JMP

17              MBR_RSM_analysis.jsl    -> JMP script: RSM fits, profiler, desirability

18   4. Python cross-check of the same analysis (quadratic RSM by least squares, scaled

19      effects, contours, Derringer desirability optimum verified with the full model).

20   Run:  python doe_runner.py

21  =====================================================================================

22  """

23  from __future__ import annotations

24

25  import csv

26  import itertools

27  import os

28  from dataclasses import asdict

29

30  import numpy as np

31  import matplotlib

32

33  matplotlib.use("Agg")

34  import matplotlib.pyplot as plt

35

36  import mbr_design as M

37

38  OUT = "mbr_outputs"

39  os.makedirs(OUT, exist_ok=True)

40

41  FACTORS = {  # name: (low, high, unit, description)

42      "MLSS_gL":    (7.0, 11.0, "g/L", "Bioreactor MLSS"),

43      "Flux20_LMH": (20.0, 30.0, "L/m2.h", "Gross design flux at 20 C"),

44      "SADm":       (0.15, 0.35, "Nm3/m2.h", "Specific membrane scour air"),

45      "Tmin_C":     (10.0, 16.0, "C", "Winter design temperature"),

46      "SRTaer_d":   (12.0, 20.0, "d", "Aerobic SRT floor"),

47  }

48  FNAMES = list(FACTORS)

49  RESPONSES = {  # name: (goal, unit, description)

50      "Energy_kWh_m3":        ("min", "kWh/m3", "Specific energy demand"),

51      "Footprint_m3":         ("min", "m3", "Bioreactor + membrane tank volume"),

52      "Membrane_area_req_m2": ("min", "m2", "Required membrane area"),

53      "Mean_TMP_bar":         ("min", "bar", "Mean TMP over 240 d"),

54      "ProcessAir_Nm3h":      ("none", "Nm3/h", "Process air, summer max-day"),

55      "Sludge_kgTSS_d":       ("none", "kg/d", "Waste sludge production"),

56      "RC_per_year":          ("none", "1/yr", "Recovery cleans per year"),

57  }

58  DESIRABILITY = ["Energy_kWh_m3", "Footprint_m3", "Membrane_area_req_m2", "Mean_TMP_bar"]

59  T_DESIGN = 12.0  # climate factor held at the site's winter design value when optimising

60

61

62  # ----------------------------------------------------------------------------------

63  def ccd_face_centred(k: int, n_center: int = 6) -> np.ndarray:

64      fact = np.array(list(itertools.product([-1, 1], repeat=k)), float)

65      axial = np.vstack([s * np.eye(k)[i] for i in range(k) for s in (-1, 1)])

66      return np.vstack([fact, axial, np.zeros((n_center, k))])

67

68

69  def decode(c: np.ndarray) -> dict:

70      return {f: (lo + hi) / 2 + c[i] * (hi - lo) / 2 for i, (f, (lo, hi, *_)) in enumerate(FACTORS.items())}

71

72

73  def encode(x: dict) -> np.ndarray:

74      return np.array([(x[f] - (lo + hi) / 2) / ((hi - lo) / 2) for f, (lo, hi, *_) in FACTORS.items()])

75

76

77  def run_model(x: dict, with_fouling: bool = True) -> dict:

78      inf = M.Influent(T_min=x["Tmin_C"])

79      d = M.DesignBasis(X_bio=x["MLSS_gL"], SRT_aer_floor=x["SRTaer_d"])

80      k = M.Kinetics()

81      J = x["Flux20_LMH"]

82      m = M.MembraneSpec(J_avg20=J, J_mm20=1.2 * J, J_peak20=1.6 * J, SAD_m=x["SADm"])

83      mem = M.membrane_design(inf, m)

84      bio = M.biological_design(inf, d, k, mem)

85      AOR = M.oxygen_demand(inf, k, bio)

86      aer = M.aeration_design(inf, d, m, bio, mem, AOR)

87      E = M.energy_balance(inf.Q_avg, aer["design_air_Nm3h"] / 1.25, mem["air_scour_Nm3h"], bio["V_anox"],

88                           d.R_ras, bio["IR"], d.sub_diffuser, m.scour_sub, 0.75, 0.70, d.anox_mix_W_m3)

89      out = {

90          "Energy_kWh_m3": E["kWh_m3"]["TOTAL"],

91          "Footprint_m3": bio["V_bio"] + mem["V_mt"],

92          "Membrane_area_req_m2": mem["A_req"],

93          "ProcessAir_Nm3h": aer["design_air_Nm3h"],

94          "Sludge_kgTSS_d": bio["Px_TSS"],

95      }

96      if with_fouling:

97          sim = M.fouling_simulation(inf, m, mem, X_mt=bio["X_mt"])

98          n_rc = sum(1 for _, e in sim["events"] if e == "RC")

99          out["Mean_TMP_bar"] = float(sim["TMP"].mean())

100          out["RC_per_year"] = n_rc * 365 / 240

101      return out

102

103

104  # ----------------------------------------------------------------------------------

105  # Quadratic response-surface model (same model JMP fits with '& RS' effects)

106  # ----------------------------------------------------------------------------------

107  TERMS = (["Intercept"] + FNAMES + [f"{a}*{b}" for a, b in itertools.combinations(FNAMES, 2)]

108           + [f"{a}*{a}" for a in FNAMES])

109

110

111  def model_matrix(C: np.ndarray) -> np.ndarray:

112      cols = [np.ones(len(C))] + [C[:, i] for i in range(5)]

113      cols += [C[:, i] * C[:, j] for i, j in itertools.combinations(range(5), 2)]

114      cols += [C[:, i] ** 2 for i in range(5)]

115      return np.column_stack(cols)

116

117

118  def fit_rsm(C, y):

119      X = model_matrix(C)

120      beta, *_ = np.linalg.lstsq(X, y, rcond=None)

121      yhat = X @ beta

122      ss_res, ss_tot = np.sum((y - yhat) ** 2), np.sum((y - y.mean()) ** 2)

123      n, p = X.shape

124      r2 = 1 - ss_res / ss_tot

125      return dict(beta=beta, r2=r2, r2adj=1 - (1 - r2) * (n - 1) / (n - p), rmse=np.sqrt(ss_res / (n - p)))

126

127

128  def desirability_min(y, lo, hi):

129      return np.clip((hi - y) / (hi - lo), 0, 1)

130

131

132  # ----------------------------------------------------------------------------------

133  def write_jsl(limits: dict, fname: str):

134      eff_main = ", ".join(f":{f} & RS" for f in FNAMES)

135      eff_int = ", ".join(f":{a} * :{b}" for a, b in itertools.combinations(FNAMES, 2))

136      eff_quad = ", ".join(f":{f} * :{f}" for f in FNAMES)

137      coding = "\n".join(f'Column( dt, "{f}" ) << Set Property( "Coding", {{{lo}, {hi}}} );'

138                         for f, (lo, hi, *_) in FACTORS.items())

139      units = "\n".join(f'Column( dt, "{n}" ) << Set Property( "Units", "{u}" );'

140                        for n, (_, u, _d) in RESPONSES.items())

141      lims = "\n".join(

142          f'Column( dt, "{r}" ) << Set Property( "Response Limits", {{Goal( Minimize ), '

143          f'Lower( {lo:.6g}, 0.9819 ), Middle( {(lo+hi)/2:.6g}, 0.5 ), Upper( {hi:.6g}, 0.0183 ), Importance( 1 )}} );'

144          for r, (lo, hi) in limits.items())

145      ys = ", ".join(f'"{r}"' for r in RESPONSES)

146      pred_cols = ", ".join(f':Name( "Pred Formula {r}" )' for r in DESIRABILITY)

147      jsl = f"""// =====================================================================

148  // MBR_RSM_analysis.jsl

149  // Response-surface analysis of the MBR preliminary-design DOE

150  // (generated by doe_runner.py - 48-run face-centred CCD, 5 factors)

151  //

152  // HOW TO RUN: put this file and mbr_doe_runs.csv in the same folder,

153  // open this script in JMP (16 or later) and press Run Script (Ctrl+R).

154  // =====================================================================

155  Names Default To Here( 1 );

156

157  // ---- 1. Open the DOE table (same folder as script; otherwise ask) ----

158  dt = Try(

159      Open( "mbr_doe_runs.csv" ),

160      Open( Pick File( "Select mbr_doe_runs.csv", "", {{"CSV Files|csv", "All Files|*"}} ) )

161  );

162  dt << Set Name( "MBR DOE - face-centred CCD" );

163

164  // ---- 2. Factor coding (coefficients in coded -1..+1 units) ----------

165  {coding}

166

167  // ---- 3. Units and desirability limits (smaller-is-better) -----------

168  {units}

169  {lims}

170

171  // ---- 4. Quadratic response-surface model for every response ---------

172  ys = {{{ys}}};

173  fits = {{}};

174  For( i = 1, i <= N Items( ys ), i++,

175      f = Eval(

176          Substitute(

177                  Expr(

178                      dt << Fit Model(

179                          Y( _Y_ ),

180                          Effects( {eff_main},

181                              {eff_int},

182                              {eff_quad} ),

183                          Personality( "Standard Least Squares" ),

184                          Emphasis( "Effect Screening" ),

185                          Run()

186                      )

187                  ),

188              Expr( _Y_ ), Parse( ":" || ys[i] )

189          )

190      );

191      f << Prediction Formula;          // saves "Pred Formula <response>"

192      Insert Into( fits, f );

193      // carry desirability limits over to the saved formula column

194      lim = Column( dt, ys[i] ) << Get Property( "Response Limits" );

195      If( !Is Empty( lim ),

196          pc = Column( dt, "Pred Formula " || ys[i] );

197          Eval( Eval Expr( pc << Set Property( "Response Limits", Expr( lim ) ) ) );

198      );

199  );

200

201  // ---- 5. Prediction profiler + desirability optimisation -------------

202  //      Winter temperature is a climate (noise) factor: locked at {T_DESIGN:g} C,

203  //      the other four factors are optimised.

204  prof = dt << Profiler(

205      Y( {pred_cols} ),

206      Desirability Functions( 1 ),

207      Term Value( Tmin_C( {T_DESIGN:g}, Lock( 1 ), Show( 1 ) ) )

208  );

209  prof << Maximize Desirability;

210

211  // ---- 6. Contour profiler: energy vs fouling trade-off --------------

212  dt << Contour Profiler(

213      Y( :Name( "Pred Formula Energy_kWh_m3" ), :Name( "Pred Formula Mean_TMP_bar" ),

214          :Name( "Pred Formula Footprint_m3" ) ),

215      Surface Plot( 1 )

216  );

217

218  // ---- 7. Raw-data overview ------------------------------------------

219  dt << Graph Builder(

220      Size( 640, 420 ),

221      Variables( X( :MLSS_gL ), Y( :Energy_kWh_m3 ), Overlay( :SADm ) ),

222      Elements( Points( X, Y, Legend( 1 ) ), Smoother( X, Y, Legend( 2 ) ) )

223  );

224  """

225      with open(fname, "w") as fh:

226          fh.write(jsl)

227

228

229  # ----------------------------------------------------------------------------------

230  def main():

231      rng = np.random.default_rng(2026)

232      C = ccd_face_centred(5, n_center=6)

233      order = rng.permutation(len(C))

234      rows = []

235      for run_no, idx in enumerate(order, 1):

236          c = C[idx]

237          x = decode(c)

238          pattern = "".join("0" if v == 0 else ("+" if v > 0 else "-") for v in c)

239          if pattern == "00000":

240              pattern = "0"

241          elif np.count_nonzero(c) == 1:

242              pattern = "".join("A" if v > 0 else ("a" if v < 0 else "0") for v in c)

243          rows.append({"Run": run_no, "Pattern": pattern, **{f: round(x[f], 4) for f in FNAMES},

244                       **run_model(x)})

245          print(f"run {run_no:2d}/{len(C)}  {pattern:6s}  E={rows[-1]['Energy_kWh_m3']:.3f}  "

246                f"TMP={rows[-1]['Mean_TMP_bar']:.3f}")

247

248      with open(f"{OUT}/mbr_doe_runs.csv", "w", newline="") as fh:

249          w = csv.DictWriter(fh, fieldnames=list(rows[0]))

250          w.writeheader()

251          for r in rows:

252              w.writerow({k: (round(v, 5) if isinstance(v, float) else v) for k, v in r.items()})

253

254      Cc = np.array([encode(r) for r in rows])

255      Y = {r: np.array([row[r] for row in rows]) for r in RESPONSES}

256      limits = {r: (float(Y[r].min()), float(Y[r].max())) for r in DESIRABILITY}

257      write_jsl(limits, f"{OUT}/MBR_RSM_analysis.jsl")

258

259      # ---------------- Python cross-check of the JMP analysis -------------------

260      fits = {r: fit_rsm(Cc, Y[r]) for r in RESPONSES}

261

262      # (a) scaled effects (coded coefficients) - equivalent of JMP 'Scaled Estimates'

263      fig, axs = plt.subplots(2, 2, figsize=(15, 10))

264      for ax, r in zip(axs.flat, DESIRABILITY):

265          b = fits[r]["beta"][1:]

266          o = np.argsort(np.abs(b))[::-1][:10][::-1]

267          names = np.array(TERMS[1:])[o]

268          ax.barh(names, b[o], color=["#c0392b" if v > 0 else "#1f4e79" for v in b[o]])

269          ax.axvline(0, color="k", lw=.8)

270          ax.set_title(f"{r}   (R² = {fits[r]['r2']:.4f}, R²adj = {fits[r]['r2adj']:.4f})", fontsize=10)

271          ax.set_xlabel(f"Scaled estimate ({RESPONSES[r][1]} per coded unit)")

272          ax.grid(axis="x", alpha=.3)

273      fig.suptitle("Quadratic RSM - ten largest scaled effects per response (red = increases response)",

274                   weight="bold")

275      fig.tight_layout(); fig.savefig(f"{OUT}/06_doe_scaled_effects.png", dpi=150); plt.close(fig)

276

277      # (b) desirability optimum (Tmin locked at design value) on fitted surfaces

278      n = 200_000

279      S = rng.uniform(-1, 1, (n, 5))

280      S[:, FNAMES.index("Tmin_C")] = encode({**{f: (FACTORS[f][0] + FACTORS[f][1]) / 2 for f in FNAMES},

281                                             "Tmin_C": T_DESIGN})[FNAMES.index("Tmin_C")]

282      Xs = model_matrix(S)

283      D = np.ones(n)

284      for r in DESIRABILITY:

285          D *= desirability_min(Xs @ fits[r]["beta"], *limits[r])

286      D = D ** (1 / len(DESIRABILITY))

287      best = S[np.argmax(D)]

288      x_opt = decode(best)

289      pred = {r: float(model_matrix(best[None])[0] @ fits[r]["beta"]) for r in RESPONSES}

290      actual = run_model(x_opt)

291      base = run_model({f: v for f, v in zip(FNAMES, [9.0, 25.0, 0.25, 12.0, 15.0])})

292

293      # (c) contour plots of fitted surfaces vs MLSS & flux (SAD_m, SRT at optimum, T = 12)

294      g = np.linspace(-1, 1, 81)

295      G1, G2 = np.meshgrid(g, g)

296      grid = np.tile(best, (G1.size, 1))

297      grid[:, 0], grid[:, 1] = G1.ravel(), G2.ravel()

298      Xg = model_matrix(grid)

299      mx = FACTORS["MLSS_gL"][0] + (g + 1) / 2 * (FACTORS["MLSS_gL"][1] - FACTORS["MLSS_gL"][0])

300      fx = FACTORS["Flux20_LMH"][0] + (g + 1) / 2 * (FACTORS["Flux20_LMH"][1] - FACTORS["Flux20_LMH"][0])

301      fig, axs = plt.subplots(2, 2, figsize=(14, 11))

302      Dg = np.ones(G1.size)

303      for ax, r, cm in zip(axs.flat[:3], ["Energy_kWh_m3", "Mean_TMP_bar", "Footprint_m3"],

304                           ["YlOrRd", "PuRd", "Blues"]):

305          Z = (Xg @ fits[r]["beta"]).reshape(G1.shape)

306          cf = ax.contourf(mx, fx, Z, 18, cmap=cm)

307          cs = ax.contour(mx, fx, Z, 9, colors="k", linewidths=.5); ax.clabel(cs, fontsize=7, fmt="%.3g")

308          fig.colorbar(cf, ax=ax, label=RESPONSES[r][1])

309          ax.plot(x_opt["MLSS_gL"], x_opt["Flux20_LMH"], "*", ms=18, mec="k", mfc="gold")

310          ax.set_title(r); ax.set_xlabel("MLSS (g/L)"); ax.set_ylabel("Flux @20°C (L/m²·h)")

311      for r in DESIRABILITY:

312          Dg *= desirability_min(Xg @ fits[r]["beta"], *limits[r])

313      Dg = (Dg ** (1 / len(DESIRABILITY))).reshape(G1.shape)

314      cf = axs[1, 1].contourf(mx, fx, Dg, 18, cmap="viridis")

315      fig.colorbar(cf, ax=axs[1, 1], label="overall desirability D")

316      axs[1, 1].plot(x_opt["MLSS_gL"], x_opt["Flux20_LMH"], "*", ms=18, mec="k", mfc="gold")

317      axs[1, 1].set_title("Overall desirability (energy, footprint, area, TMP)")

318      axs[1, 1].set_xlabel("MLSS (g/L)"); axs[1, 1].set_ylabel("Flux @20°C (L/m²·h)")

319      fig.suptitle(f"Fitted response surfaces at SAD_m = {x_opt['SADm']:.3f}, SRT_aer = {x_opt['SRTaer_d']:.1f} d, "

320                   f"T = {T_DESIGN:g} °C   (★ = desirability optimum)", weight="bold")

321      fig.tight_layout(); fig.savefig(f"{OUT}/07_rsm_contours.png", dpi=150); plt.close(fig)

322

323      # (d) prediction-profiler style traces around the optimum

324      fig, axs = plt.subplots(len(DESIRABILITY), 5, figsize=(17, 11), sharex="col")

325      for j, f in enumerate(FNAMES):

326          sweep = np.tile(best, (61, 1)); sweep[:, j] = np.linspace(-1, 1, 61)

327          xs = FACTORS[f][0] + (sweep[:, j] + 1) / 2 * (FACTORS[f][1] - FACTORS[f][0])

328          for i, r in enumerate(DESIRABILITY):

329              ax = axs[i, j]

330              ax.plot(xs, model_matrix(sweep) @ fits[r]["beta"], color="#1f4e79", lw=2)

331              ax.axvline(x_opt[f], color="#c0392b", ls="--", lw=1)

332              ax.grid(alpha=.3)

333              if j == 0: ax.set_ylabel(r.replace("_", "\n", 1), fontsize=9)

334              if i == len(DESIRABILITY) - 1: ax.set_xlabel(f"{f}\n= {x_opt[f]:.3g}", fontsize=9)

335      fig.suptitle("Prediction profiler (Python equivalent of the JMP Profiler) at the desirability optimum",

336                   weight="bold")

337      fig.tight_layout(); fig.savefig(f"{OUT}/08_prediction_profiler.png", dpi=150); plt.close(fig)

338

339      # ---------------- summary -------------------------------------------------

340      lines = ["# DOE / response-surface results (Python cross-check of the JMP analysis)\n",

341               f"Design: face-centred CCD, 5 factors, {len(rows)} runs (32 factorial + 10 axial + 6 centre).\n",

342               "## Model fit (full quadratic, 21 terms)",

343               "| Response | R² | R² adj | RMSE |", "|---|---|---|---|"]

344      lines += [f"| {r} | {fits[r]['r2']:.4f} | {fits[r]['r2adj']:.4f} | {fits[r]['rmse']:.4g} |" for r in RESPONSES]

345      lines += ["\n## Desirability optimum (Tmin locked at 12 °C)",

346                f"Overall desirability D = {D.max():.3f}\n",

347                "| Factor | Optimum | Baseline design |", "|---|---|---|"]

348      lines += [f"| {f} | {x_opt[f]:.3g} | {v} |" for f, v in zip(FNAMES, [9.0, 25.0, 0.25, 12.0, 15.0])]

349      lines += ["\n| Response | RSM prediction | Full model at optimum | Baseline design |", "|---|---|---|---|"]

350      lines += [f"| {r} | {pred[r]:.4g} | {actual[r]:.4g} | {base[r]:.4g} |" for r in RESPONSES]

351      with open(f"{OUT}/doe_summary.md", "w") as fh:

352          fh.write("\n".join(lines))

353      print("\n".join(lines))

354

355

356  if __name__ == "__main__":

357      main()

358

# Appendix C. MBR_RSM_analysis.jsl: JMP analysis script

Generated by doe_runner.py. Run in JMP 16 or later together with mbr_doe_runs.csv.

1  // =====================================================================

2  // MBR_RSM_analysis.jsl

3  // Response-surface analysis of the MBR preliminary-design DOE

4  // (generated by doe_runner.py - 48-run face-centred CCD, 5 factors)

5  //

6  // HOW TO RUN: put this file and mbr_doe_runs.csv in the same folder,

7  // open this script in JMP (16 or later) and press Run Script (Ctrl+R).

8  // =====================================================================

9  Names Default To Here( 1 );

10

11  // ---- 1. Open the DOE table (same folder as script; otherwise ask) ----

12  dt = Try(

13      Open( "mbr_doe_runs.csv" ),

14      Open( Pick File( "Select mbr_doe_runs.csv", "", {"CSV Files|csv", "All Files|*"} ) )

15  );

16  dt << Set Name( "MBR DOE - face-centred CCD" );

17

18  // ---- 2. Factor coding (coefficients in coded -1..+1 units) ----------

19  Column( dt, "MLSS_gL" ) << Set Property( "Coding", {7.0, 11.0} );

20  Column( dt, "Flux20_LMH" ) << Set Property( "Coding", {20.0, 30.0} );

21  Column( dt, "SADm" ) << Set Property( "Coding", {0.15, 0.35} );

22  Column( dt, "Tmin_C" ) << Set Property( "Coding", {10.0, 16.0} );

23  Column( dt, "SRTaer_d" ) << Set Property( "Coding", {12.0, 20.0} );

24

25  // ---- 3. Units and desirability limits (smaller-is-better) -----------

26  Column( dt, "Energy_kWh_m3" ) << Set Property( "Units", "kWh/m3" );

27  Column( dt, "Footprint_m3" ) << Set Property( "Units", "m3" );

28  Column( dt, "Membrane_area_req_m2" ) << Set Property( "Units", "m2" );

29  Column( dt, "Mean_TMP_bar" ) << Set Property( "Units", "bar" );

30  Column( dt, "ProcessAir_Nm3h" ) << Set Property( "Units", "Nm3/h" );

31  Column( dt, "Sludge_kgTSS_d" ) << Set Property( "Units", "kg/d" );

32  Column( dt, "RC_per_year" ) << Set Property( "Units", "1/yr" );

33  Column( dt, "Energy_kWh_m3" ) << Set Property( "Response Limits", {Goal( Minimize ), Lower( 0.481564, 0.9819 ), Middle( 0.710142, 0.5 ), Upper( 0.93872, 0.0183 ), Importance( 1 )} );

34  Column( dt, "Footprint_m3" ) << Set Property( "Response Limits", {Goal( Minimize ), Lower( 5457.27, 0.9819 ), Middle( 9478.24, 0.5 ), Upper( 13499.2, 0.0183 ), Importance( 1 )} );

35  Column( dt, "Membrane_area_req_m2" ) << Set Property( "Response Limits", {Goal( Minimize ), Lower( 27450.6, 0.9819 ), Middle( 37893.8, 0.5 ), Upper( 48337, 0.0183 ), Importance( 1 )} );

36  Column( dt, "Mean_TMP_bar" ) << Set Property( "Response Limits", {Goal( Minimize ), Lower( 0.0717862, 0.9819 ), Middle( 0.105542, 0.5 ), Upper( 0.139297, 0.0183 ), Importance( 1 )} );

37

38  // ---- 4. Quadratic response-surface model for every response ---------

39  ys = {"Energy_kWh_m3", "Footprint_m3", "Membrane_area_req_m2", "Mean_TMP_bar", "ProcessAir_Nm3h", "Sludge_kgTSS_d", "RC_per_year"};

40  fits = {};

41  For( i = 1, i <= N Items( ys ), i++,

42      f = Eval(

43          Substitute(

44                  Expr(

45                      dt << Fit Model(

46                          Y( _Y_ ),

47                          Effects( :MLSS_gL & RS, :Flux20_LMH & RS, :SADm & RS, :Tmin_C & RS, :SRTaer_d & RS,

48                              :MLSS_gL * :Flux20_LMH, :MLSS_gL * :SADm, :MLSS_gL * :Tmin_C, :MLSS_gL * :SRTaer_d, :Flux20_LMH * :SADm, :Flux20_LMH * :Tmin_C, :Flux20_LMH * :SRTaer_d, :SADm * :Tmin_C, :SADm * :SRTaer_d, :Tmin_C * :SRTaer_d,

49                              :MLSS_gL * :MLSS_gL, :Flux20_LMH * :Flux20_LMH, :SADm * :SADm, :Tmin_C * :Tmin_C, :SRTaer_d * :SRTaer_d ),

50                          Personality( "Standard Least Squares" ),

51                          Emphasis( "Effect Screening" ),

52                          Run()

53                      )

54                  ),

55              Expr( _Y_ ), Parse( ":" || ys[i] )

56          )

57      );

58      f << Prediction Formula;          // saves "Pred Formula <response>"

59      Insert Into( fits, f );

60      // carry desirability limits over to the saved formula column

61      lim = Column( dt, ys[i] ) << Get Property( "Response Limits" );

62      If( !Is Empty( lim ),

63          pc = Column( dt, "Pred Formula " || ys[i] );

64          Eval( Eval Expr( pc << Set Property( "Response Limits", Expr( lim ) ) ) );

65      );

66  );

67

68  // ---- 5. Prediction profiler + desirability optimisation -------------

69  //      Winter temperature is a climate (noise) factor: locked at 12 C,

70  //      the other four factors are optimised.

71  prof = dt << Profiler(

72      Y( :Name( "Pred Formula Energy_kWh_m3" ), :Name( "Pred Formula Footprint_m3" ), :Name( "Pred Formula Membrane_area_req_m2" ), :Name( "Pred Formula Mean_TMP_bar" ) ),

73      Desirability Functions( 1 ),

74      Term Value( Tmin_C( 12, Lock( 1 ), Show( 1 ) ) )

75  );

76  prof << Maximize Desirability;

77

78  // ---- 6. Contour profiler: energy vs fouling trade-off --------------

79  dt << Contour Profiler(

80      Y( :Name( "Pred Formula Energy_kWh_m3" ), :Name( "Pred Formula Mean_TMP_bar" ),

81          :Name( "Pred Formula Footprint_m3" ) ),

82      Surface Plot( 1 )

83  );

84

85  // ---- 7. Raw-data overview ------------------------------------------

86  dt << Graph Builder(

87      Size( 640, 420 ),

88      Variables( X( :MLSS_gL ), Y( :Energy_kWh_m3 ), Overlay( :SADm ) ),

89      Elements( Points( X, Y, Legend( 1 ) ), Smoother( X, Y, Legend( 2 ) ) )

90  );

91

# Appendix D. DOE run table (mbr_doe_runs.csv)

Units: MLSS g/L; flux L/m²·h at 20 °C; SAD_m Nm³/m²·h; T °C; SRT d; energy kWh/m³; footprint m³; area m²; TMP bar (240-day mean); RC/yr recovery cleans per year. Process air and sludge production columns are in the CSV file. Pattern: 0 = centre point, a/A = axial low/high, −/+ = factorial levels.

| Run | Pattern | MLSS | Flux | SAD_m | T | SRT | Energy | Footprint | Area | TMP | RC/yr |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 0 | 9 | 25 | 0.25 | 13 | 16 | 0.660 | 8,591 | 35,632 | 0.115 | 1.5 |
| 2 | 00a00 | 9 | 25 | 0.15 | 13 | 16 | 0.560 | 8,591 | 35,632 | 0.125 | 3.0 |
| 3 | +++-+ | 11 | 30 | 0.35 | 10 | 20 | 0.762 | 8,549 | 32,225 | 0.121 | 3.0 |
| 4 | 0000a | 9 | 25 | 0.25 | 13 | 12 | 0.647 | 6,871 | 35,632 | 0.115 | 1.5 |
| 5 | ---++ | 7 | 20 | 0.15 | 16 | 20 | 0.554 | 12,953 | 41,176 | 0.115 | 1.5 |
| 6 | +--+- | 11 | 20 | 0.15 | 16 | 12 | 0.629 | 5,457 | 41,176 | 0.108 | 3.0 |
| 7 | 0A000 | 9 | 30 | 0.25 | 13 | 16 | 0.618 | 8,612 | 29,693 | 0.129 | 3.0 |
| 8 | --++- | 7 | 20 | 0.35 | 16 | 12 | 0.768 | 8,665 | 41,176 | 0.100 | 0.0 |
| 9 | -++-- | 7 | 30 | 0.35 | 10 | 12 | 0.648 | 9,896 | 32,225 | 0.127 | 1.5 |
| 10 | -+--+ | 7 | 30 | 0.15 | 10 | 20 | 0.498 | 13,499 | 32,225 | 0.139 | 6.1 |
| 11 | --+-+ | 7 | 20 | 0.35 | 10 | 20 | 0.840 | 13,436 | 48,337 | 0.072 | 0.0 |
| 12 | 0000A | 9 | 25 | 0.25 | 13 | 20 | 0.670 | 10,253 | 35,632 | 0.115 | 1.5 |
| 13 | -+--- | 7 | 30 | 0.15 | 10 | 12 | 0.482 | 9,896 | 32,225 | 0.139 | 6.1 |
| 14 | ++--+ | 11 | 30 | 0.15 | 10 | 20 | 0.594 | 8,549 | 32,225 | 0.138 | 9.1 |
| 15 | +---+ | 11 | 20 | 0.15 | 10 | 20 | 0.669 | 8,486 | 48,337 | 0.100 | 1.5 |
| 16 | +---- | 11 | 20 | 0.15 | 10 | 12 | 0.648 | 6,193 | 48,337 | 0.100 | 1.5 |
| 17 | +--++ | 11 | 20 | 0.15 | 16 | 20 | 0.654 | 8,186 | 41,176 | 0.108 | 3.0 |
| 18 | -+-++ | 7 | 30 | 0.15 | 16 | 20 | 0.504 | 12,995 | 27,451 | 0.128 | 6.1 |
| 19 | 0 | 9 | 25 | 0.25 | 13 | 16 | 0.660 | 8,591 | 35,632 | 0.115 | 1.5 |
| 20 | 000a0 | 9 | 25 | 0.25 | 10 | 16 | 0.656 | 8,768 | 38,670 | 0.121 | 1.5 |
| 21 | -+-+- | 7 | 30 | 0.15 | 16 | 12 | 0.484 | 8,707 | 27,451 | 0.128 | 6.1 |
| 22 | A0000 | 11 | 25 | 0.25 | 13 | 16 | 0.714 | 7,005 | 35,632 | 0.126 | 1.5 |
| 23 | ---+- | 7 | 20 | 0.15 | 16 | 12 | 0.534 | 8,665 | 41,176 | 0.115 | 1.5 |
| 24 | ++++- | 11 | 30 | 0.35 | 16 | 12 | 0.746 | 5,499 | 27,451 | 0.110 | 3.0 |
| 25 | 0 | 9 | 25 | 0.25 | 13 | 16 | 0.660 | 8,591 | 35,632 | 0.115 | 1.5 |
| 26 | +-+-+ | 11 | 20 | 0.35 | 10 | 20 | 0.939 | 8,486 | 48,337 | 0.083 | 0.0 |
| 27 | +-++- | 11 | 20 | 0.35 | 16 | 12 | 0.864 | 5,457 | 41,176 | 0.117 | 0.0 |
| 28 | ----+ | 7 | 20 | 0.15 | 10 | 20 | 0.573 | 13,436 | 48,337 | 0.113 | 0.0 |
| 29 | ++-++ | 11 | 30 | 0.15 | 16 | 20 | 0.604 | 8,228 | 27,451 | 0.134 | 7.6 |
| 30 | ----- | 7 | 20 | 0.15 | 10 | 12 | 0.557 | 9,833 | 48,337 | 0.113 | 0.0 |
| 31 | a0000 | 7 | 25 | 0.25 | 13 | 16 | 0.617 | 11,084 | 35,632 | 0.106 | 1.5 |
| 32 | ++--- | 11 | 30 | 0.15 | 10 | 12 | 0.572 | 6,256 | 32,225 | 0.138 | 9.1 |
| 33 | +-+-- | 11 | 20 | 0.35 | 10 | 12 | 0.917 | 6,193 | 48,337 | 0.083 | 0.0 |
| 34 | -++-+ | 7 | 30 | 0.35 | 10 | 20 | 0.665 | 13,499 | 32,225 | 0.127 | 1.5 |
| 35 | 0a000 | 9 | 20 | 0.25 | 13 | 16 | 0.702 | 8,570 | 44,540 | 0.101 | 1.5 |
| 36 | -++++ | 7 | 30 | 0.35 | 16 | 20 | 0.671 | 12,995 | 27,451 | 0.116 | 1.5 |
| 37 | -+++- | 7 | 30 | 0.35 | 16 | 12 | 0.651 | 8,707 | 27,451 | 0.116 | 1.5 |
| 38 | +-+++ | 11 | 20 | 0.35 | 16 | 20 | 0.890 | 8,186 | 41,176 | 0.117 | 0.0 |
| 39 | 0 | 9 | 25 | 0.25 | 13 | 16 | 0.660 | 8,591 | 35,632 | 0.115 | 1.5 |
| 40 | +++-- | 11 | 30 | 0.35 | 10 | 12 | 0.741 | 6,256 | 32,225 | 0.121 | 3.0 |
| 41 | --+++ | 7 | 20 | 0.35 | 16 | 20 | 0.788 | 12,953 | 41,176 | 0.100 | 0.0 |
| 42 | ++-+- | 11 | 30 | 0.15 | 16 | 12 | 0.578 | 5,499 | 27,451 | 0.134 | 7.6 |
| 43 | +++++ | 11 | 30 | 0.35 | 16 | 20 | 0.772 | 8,228 | 27,451 | 0.110 | 3.0 |
| 44 | 00A00 | 9 | 25 | 0.35 | 13 | 16 | 0.761 | 8,591 | 35,632 | 0.100 | 1.5 |
| 45 | 0 | 9 | 25 | 0.25 | 13 | 16 | 0.660 | 8,591 | 35,632 | 0.115 | 1.5 |
| 46 | 000A0 | 9 | 25 | 0.25 | 16 | 16 | 0.623 | 8,441 | 32,941 | 0.131 | 6.1 |
| 47 | --+-- | 7 | 20 | 0.35 | 10 | 12 | 0.824 | 9,833 | 48,337 | 0.072 | 0.0 |
| 48 | 0 | 9 | 25 | 0.25 | 13 | 16 | 0.660 | 8,591 | 35,632 | 0.115 | 1.5 |